## Table of Contents
BOWIE POWER STATION MODEL 4 EMISSION WORKBOOK TABLE OF CONTENTS
Listed in the order in which tab appears, followed by a brief description
Data Tracking | Origins of Project Data
Bowie Sources | General information about the equipment
Emission Factor List | Sources for determining emissions
Annual Project Total Emissions
Ann Crit Emiss Summar-uncontrol
One Hour Emission Crit Summary | Provides one hour emission totals for normal and startup operation
Annual HAP Summary
Turbine and Duct Burner Hourly | Emissions given for several different situations, temps, loads, uncontrolled/controlled
Turbine and Duct Burner Annual | Emissions given for several different situations, uncontrolled/controlled
Turbine Startup Emissions
Turbine Shutdown Emissions
Turbine and DB Heat Input
Turbine HAP Emissions | Emissions given in uncontrolled-hourly and controlled-annually
Duct Burner HAP Emissions | Emissions given in uncontrolled-hourly and controlled-annually
Turbine+Duct Burner HAPs | Given in tons/year
Aux Boiler Emissions | Parameters and Emissions
Emergency Fire Pump Emissions | Parameters and Emissions
Cooling Tower | Parameters and PM/PM10/PM2.5 emissions
Cooling Tower HAPs
Evaporation Pond Emissions
GHG Emissions | Listed by each piece of equipment and in total
Modeling Data Summary
Modeling - Screening Parameters
Turbine+Duct Burner Stack Info | Parameters
Turbine Stack Data Weighted Ave | Average stack weighted parameters
24-hour Crit Emissions Summary | Given for several scenarios

## Bowie Sources
BOWIE POWER STATION MODEL 4 EMISSION UNITS
Type of Equipment | Number | Size | Units | Capacity Factor/hours of operation for Each Piece of Equipment | Units
GE Frame 7FA Model 4 Natural Gas-Fired Combined Cycle Combustion Turbines | 2 | 3469.12 | mmBtu/hour (HHV) both
|  | 1734.56 | mmBtu/hour (HHV) each | 95% |  | Maximum heat input for both turbines divided by 2
Duct Burners | 2 | 420 | mmBtu/hour (HHV) | 4224 | hours
Natural Gas-Fired Auxiliary Boilers | 1 | 50 | mmBtu/hour | 450 | hours
Diesel-Fired Fire Pumps | 1 | 260 | horsepower | 100 | hours | Hours limit from 40 CFR 60.4211(f)(2)
Cooling Tower | 1 | 9 | cells/tower | 100%
|  | 127860 | gallons/min circulating rate
Evaporation Pond | 1 | 127 | gallons/min max cooling tower blowdown | 100%
|  | 4 | gallons/min stormwater
|  | 131 | gallons/min |  |  | Maximum cooling tower blowdown + stormwater
Circuit Breakers Containing SF6 | 5
Turbine and Duct Burner volatile HAP emissions control |  |  | 70%
Fuel Data
Fuel | Heat Content |  | Sulfur Content
Natural Gas | 1034.6 | Btu/scf | 0.75 | grains/100 scf | from El Paso Corporation
Diesel Fuel | 137000 | Btu/gallon | 15 | ppm | Diesel BTU content from AP-42, Appendix A, Page A-5 Diesel sulfur content required by 40 CFR Subpart IIII 60.4207(b) which refers to 80.510(b)

## Emission Factor List
BOWIE POWER STATION - MODEL 4 EMISSION REFERENCE SUMMARY LIST
TURBINE
Normal Operation:
NOx, CO, VOCs and SO2 - provided by Kiewit Power Engineers Co. based on Gatecycle Modeling
PM/PM10/PM2.5 - based on sulfur content of fuel, source testing of similar combustion turbines, and the results of the best available control technology analysis
HAPs - AP-42, Section 3.1, Table 3.1-3, April 2000
Startup/Shutdown
NOx, CO, VOCs - values from Kiewit Power Engineers Co.
SO2 and PM/PM10/PM2.5 - Assume same as normal operations
DUCT BURNERS
Criteria Pollutants except for PM/PM10/PM2.5- from Kiewit Power Engineers Co.
PM/PM10/PM2.5 - based on sulfur content of fuel, source testing of similar units, and the results of the best available control technology analysis
HAPs - AP-42, Section 1.4, Tables 1.4-2, -3, and -4, July 1998
AUXILIARY BOILER
NOx, CO, VOC, PM/PM10/PM2.5 provided by Rentech
SO2 - AP-42, Section 1.4, Table 1.4-2, July 1998, adjusted based on natural gas sulfur content from El Paso Natural Gas
HAPs - AP-42, Section 1.4 Tables 1.4-3 and -4, July 1998
EMERGENCY FIRE PUMP
NOx, CO, VOC, PM/PM10/PM2.5 - Cummins CFP9E-F10 Fire Power Engine Specification Sheet
SO2 AP-42, Section 3.4, Table 3.4-1, October 1996
HAPs - AP-42, Section 3.3, Table 3.3-2 and WebFIRE
COOLING TOWERS
PM10 - Based on design of drift eliminators, cooling tower circulating rate, and total dissolved solids content of water. Percentage of PM that is PM10 based on calculation from 2001 AWMA paper. Droplet Distribution for drift eliminators from Marley
HAPs (except chloroform) - based on cooling tower drift and content of blowdown
Chloroform - from EPA's, Locating and Estimating Air Emissions from Sources of Chloroform
EVAPORATION PONDS
Chloroform - from EPA's, Locating and Estimating Air Emissions from Sources of Chloroform
GHG Emissions
CO2 - 40 Code of Federal Regulations 98, Table C-1, "Default CO2 Emission Factors and High Heat Values for Various Types of Fuel".
CH4 and N20 - 40 Code of Federal Regulations 98, Table C-2, "Default CH4 and N2O Emission Factors for Various Types of Fuel".
Global Warming Potentials - From 40 CFR 98, Table A-1 "Global Warming Potentials"
Substation Leak Rate from Electric Power Substation Engineering, 2nd Edition, 2007, Edited by John D. McDonald. "Field checks of GIS [gas-insulated substations] in service after many years of service indicate that a leak rate objective lower than 0.1% per year is obtainable".

## Annual Project Total Emissions
BOWIE POWER STATION - MODEL 4 ANNUAL PROJECT CRITERIA POLLUTANT EMISSIONS
Equipment
Turbines and Duct Burners | 2
Auxiliary Boilers | 1
Emergency Fire Pumps | 1
Cooling Towers | 1
Evaporation Pond | 1
Circuit Breakers | 5
Annual Criteria Pollutant Emissions - Per Piece of Equipment
Emissions (tons/year)
| NOx | CO | VOC | SO2 | PM | PM10 | PM2.5 | CO2 | CH4 | N2O | SF6 | CO2e
Per Turbine and Duct Burner Pair | 69.4672 | 80.542 | 14.9708 | 15.0013 | 31.2705 | 31.2705 | 31.2705 | 875542.2522 | 16.5085 | 1.6508 | --- | 876400.6917
Per Auxiliary Boiler | 0.12375 | 0.41625 | 0.045 | 0.024466 | 0.07875 | 0.07875 | 0.07875 | 1315.2274 | 0.024806 | 0.0024806 | --- | 1316.5173
Per Emergency Fire Pump | 0.063053 | 0.040612 | 0.0035252 | 0.00015776 | 0.0033819 | 0.0033819 | 0.0033819 | 14.9693 | 0.00060719 | 0.00012144 | --- | 15.0197
Per Cooling Tower | --- | --- | 0.6449 | --- | 5.67 | 3.8253 | 1.823 | --- | --- | --- | --- | ---
Evaporation Ponds | --- | --- | 0.00021545 | --- | --- | --- | --- | --- | --- | --- | --- | ---
Circuit Breakers | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.00018 | 4.302
Annual Criteria Pollutant Emissions - Per Equipment Type
Total Project Emissions (tons/year)
Emission Source | NOx | CO | VOC | SO2 | PM | PM10 | PM2.5 | CO2 | CH4 | N2O | SF6 | CO2e
Turbine and Duct Burner Total | 138.9343 | 161.0839 | 29.9417 | 30.0026 | 62.541 | 62.541 | 62.541 | 1751084.5044 | 33.0169 | 3.3017 | --- | 1752801.3834
Auxiliary Boiler Total | 0.12375 | 0.41625 | 0.045 | 0.024466 | 0.07875 | 0.07875 | 0.07875 | 1315.2274 | 0.024806 | 0.0024806 | --- | 1316.5173
Fire Pump Total | 0.063053 | 0.040612 | 0.0035252 | 0.00015776 | 0.0033819 | 0.0033819 | 0.0033819 | 14.9693 | 0.00060719 | 0.00012144 | --- | 15.0197
Cooling Tower Total | --- | --- | 0.6449 | --- | 5.67 | 3.8253 | 1.823 | --- | --- | --- | --- | ---
Evaporation Pond Total | --- | --- | 0.00021545 | --- | --- | --- | --- | --- | --- | --- | --- | ---
Circuit Breakers | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.0009 | 21.51
Project Total | 139.1211 | 161.5408 | 30.6353 | 30.0273 | 68.2931 | 66.4485 | 64.4461 | 1752414.7011 | 33.0423 | 3.3043 | 0.0009 | 1754154.4304
TONS PER YEAR FOR EACH PIECE OF EQUIPMENT AT MAXIMUM OPERATION For turbines and duct burners: Ton/year values are from the spreadsheet titled "Combined Turbine and Duct Burner Annual Emissions" For auxiliary boiler: Ton/year values are from the spreadsheet titled "Auxiliary Boiler Data and Emissions". For emergency fire pump: Ton/year values are from the spreadsheet titled "Emergency Fire Pump Data and Emissions". For cooling tower: Tons/year value comes from the spreadsheest titled "Cooling Tower PM/PM10/PM2.5 Emissions" and "Cooling Tower HAP Emissions" For evaporation pond: Tons/year value comes from the spreadsheet titled "Evaporation Pond Chloroform Emissions". CO2, CH4, N2O, SF6, and CO2e: Tons/year values are from the spreadsheet titled "Annual Greenhouse Gas Emissions" Total Project Emissions tons = tons Each Piece of Equipment x # of Pieces of Equipment For turbines, duct burners, auxiliary boiler, and emergency fire pump assume PM10 = PM2.5
DOUBLE CHECK ON TOTAL PROJECT ANNUAL EMISSIONS FOR ABOVE CAPACITY FACTORS AND EQUIPMENT NUMBERS The double check is calculated as follows: tons = tons individual pieces of equipment x number of pieces of equipment year year tons/year for individual pieces of equipment values come from the table on the sheet labeled "Annual Emissions in Tons per Year for Each Piece of Equipment for Above Capacity.

## Ann Crit Emiss Summar-uncontrol
BOWIE POWER STATION - MODEL 4 ANNUAL CRITERIA POLLUTANT EMISSIONS SUMMARY - UNCONTROLLED
Annual Criteria Pollutant Emissions
Emissions (tons/year)
| NOx | CO | VOC | SO2 | PM | PM10 | PM2.5 | CO2 | CH4 | N2O | SF6 | CO2e
Per Turbine and Duct Burner Pair | 299.5867 | 248.6361 | 22.5601 | 15.0013 | 31.2705 | 31.2705 | 31.2705 | 875542.2522 | 16.5085 | 1.6508 | --- | 876400.6917
Per Auxiliary Boiler | 0.12375 | 0.41625 | 0.045 | 0.024466 | 0.07875 | 0.07875 | 0.07875 | 1315.2274 | 0.024806 | 0.0024806 | --- | 1316.5173
Per Emergency Fire Pump | 0.063053 | 0.040612 | 0.0035252 | 0.00015776 | 0.0033819 | 0.0033819 | 0.0033819 | 14.9693 | 0.00060719 | 0.00012144 | --- | 15.0197
Per Cooling Tower | --- | --- | 0.6449 | --- | 5.67 | 3.8253 | 1.823 | --- | --- | --- | --- | ---
Evaporation Ponds | --- | --- | 0.00021545 | --- | --- | --- | --- | --- | --- | --- | --- | ---
Per Circuit Breaker | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.00018 | 4.302
TONS PER YEAR FOR EACH PIECE OF EQUIPMENT AT MAXIMUM OPERATION For turbines and duct burners Ton/year are from the spreadsheet titled "Combined Turbine and Duct Burner Annual Emissions". For auxiliary boiler: Ton/year values are from the spreadsheet titled "Aux Boiler Data and Emissions". For emergency fire pump: Ton/year values are from the spreadsheet titled "Emergency Fire Pump Data and Emissions". For cooling tower: Tons/year value comes from the spreadsheets titled "Cooling Tower PM/PM10/PM2.5 Emissions" and Cooling Tower HAP Emissions" For evaporation ponds: Tons/year value comes from the spreadsheet titled "Evaporation Pond Chloroform Emissions". CO2, CH4, N2O, SF6, and CO2e: Tons/year values are from the spreadsheet titled "Annual Greenhouse Gas Emissions" For turbines, duct burners, auxiliary boiler, and emergency fire pump assume PM10 = PM2.5
DOUBLE CHECK ON TOTAL PROJECT ANNUAL EMISSIONS FOR ABOVE CAPACITY FACTORS AND EQUIPMENT NUMBERS The double check is calculated as follows: tons = tons individual pieces of equipment x number of pieces of equipment year year tons/year for individual pieces of equipment values come from the table on the sheet labeled "Annual Emissions in Tons per Year for Each Piece of Equipment for Above Capacity.

## One Hour Emission Crit Summary
BOWIE POWER STATION - MODEL 4 ONE-HOUR CRITERIA POLLUTANT EMISSION SUMMARY
Maximum One-Hour Emissions
Emissions (pounds/hour)
Emission Basis | Normal Operation | [6 empty] | Startup Operation
| NOx | CO | VOC | SO2 | PM | PM10 | PM2.5 | NOx | CO | VOC | SO2 | PM10/PM2.5
Per Turbine and Duct Burner Pair | 15.6 | 9.5 | 4.1 | 4.1 | 8.5 | 8.5 | 8.5 | 101.32 | 262.28 | 17.56 | 3.6 | 6.5
Per Aux. Boiler | 0.55 | 1.85 | 0.2 | 0.10874 | 0.35 | 0.35 | 0.35
Per Fire Pump | 1.2611 | 0.81223 | 0.070504 | 0.0031551 | 0.067638 | 0.067638 | 0.067638
Per Cooling Tower | --- | --- | 0.14724 | --- | 1.2945 | 0.87337 | 0.41621
Evaporation Ponds | --- | --- | 4.919e-05 | --- | --- | --- | ---
For turbines and Duct Burners: Normal operation values are from the spreadsheet titled "Combined Turbine and Duct Burner Hourly Emission Rates" Startup values for NOx, CO, and VOC are maximum values from the spreadsheet titled "Turbine Startup Emissions" Startup values for SO2 and PM10/PM2.5 are maximum turbine only (no duct firing) emissions from the spreadshee "Turbine Hourly CriteriaEmission" For auxiliary boiler: Ton/year values are from the spreadsheet titled "Auxiliary Boiler Data and Emissions". For emergency fire pump: Ton/year values are from the spreadsheet titled "Emergency Fire Pump Data and Emissions". For cooling tower: Tons/year value comes from the spreadsheets titled "Cooling Tower PM/PM10/PM2.5 Emissions" and "Cooling Tower HAP Emissions" For evaporation pond: Tons/year value comes from the spreadsheet titled "Evaporation Pond Chloroform Emissions". Total Project Emissions tons = tons Each Piece of Equipment x # of Pieces of Equipment For turbines, duct burners, auxiliary boiler, and emergency fire pump assume PM10 = PM2.5

## Annual HAP Summary
BOWIE POWER STATION - MODEL 4 ANNUAL HAP POLLUTANT EMISSION SUMMARY
Equipment
Turbines and Duct Burners | 2
Auxiliary Boilers | 1
Fire Pumps | 1
Cooling Towers | 1
Evaporation Ponds | 1
Emissions (tons/year)
Pollutant | Each Turbine and Duct Burner | Each Auxiliary Boiler | Each Emergency Fire Pump | Each Cooling Tower | Evaporation Ponds | Project Total
Acetaldehyde | 0.099066 |  | 7.0403e-05 |  |  | 0.1982
Acrolein | 0.015851 |  |  |  |  | 0.031701
Antimony |  |  |  | 5.047e-05 |  | 5.047e-05
Arsenic | 0.00017147 | 2.1748e-06 |  | 7.5705e-05 |  | 0.00042083
Benzene | 0.03026 | 2.2835e-05 | 8.564e-05 |  |  | 0.060628
Beryllium |  |  |  | 1.2618e-05 |  | 1.2618e-05
Cadmium | 0.00094311 | 1.1961e-05 |  | 5.047e-05 |  | 0.0019487
Chloroform |  |  |  | 0.6449 | 0.00021545 | 0.64511
Chromium | 0.0012003 | 1.5223e-05 |  | 0.00012618 |  | 0.002542
Cobalt | 7.2019e-05 | 9.134e-07 |  |  |  | 0.00014495
Dichlorobenzene | 0.00030865 | 1.3049e-05 |  |  |  | 0.00063036
Ethylbenzene | 0.079253 |  | 2.0569e-06 |  |  | 0.15851
Formaldehyde | 1.7777 | 0.00081553 | 0.00010831 |  |  | 3.5563
Hexane | 0.46298 | 0.019573 |  |  |  | 0.94554
Lead | 0.00042869 | 5.4369e-06 |  | 5.047e-05 |  | 0.00091328
Manganese | 0.0003258 | 4.132e-06 |  |  |  | 0.00065574
Mercury | 0.00022292 | 2.8272e-06 |  | 5.6078e-06 |  | 0.00045427
Naphthalene | 0.0033765 | 6.633e-06 | 7.7838e-06 |  |  | 0.0067675
Nickel | 0.0018005 | 2.2835e-05 |  | 0.00012618 |  | 0.00375
POMsa | 0.0054619 | 5.6326e-07 | 1.5421e-05 |  |  | 0.01094
Selenium |  |  |  | 5.047e-05 |  | 5.047e-05
Toluene | 0.32284 | 3.6971e-05 | 3.7542e-05 |  |  | 0.64575
Xylenes | 0.15851 |  | 2.616e-05 |  |  | 0.31704
|  |  |  | TOTAL FEDERAL HAPs |  | 6.5881
aNote that PAHs are a subset of POMs
ANNUAL HAP EMISSIONS IN TONS PER YEAR Values for Turbine and Duct Burners are the from the spreadsheets titled "Turbine and Duct Burner HAP Emissions" . Because PAHs are a subset of POMs, the value for POMs for the turbines and duct burners is the value for PAHs emissions. Values for Auxiliary Boiler are from the spreadsheet titled "Auxiliary Boiler Data and Emissions". Values for Emergency Fire Pump are from the spreadsheet titled "Emergency Fire Pump Data and Emissions" Values for the Cooling Tower are from the spreadsheet titled "Cooling Tower HAPs". Values for the Evaporation Pond are from the spreadsheet titled "Evaporation Pond Chloroform Emissions". Total of each pollutant for the Project is calculated as follows: tons = ( tons for each turbine x number of turbines) + (tons for each auxiliary boiler x number of auxiliary boilers) year year year + (tons for fire pump x number of fire pumps) + (tons for each cooling tower x number of cooling towers) + (tons for evaporation ponds) year year year

## Turbine and Duct Burner Hourly
BOWIE POWER STATION TURBINE AND DUCT BURNER HOURLY EMISSION RATES
Duct Burners = | 420 | mmBtu/hour maximum heat input
Duct Burners PM/PM10/PM2.5 (front and back half) | 2
Based on source testing of similar combustion turbines and the results of the Best Available Control Technology Analysis
NOx (uncontrolled) |  | lb/hour
Ambient Temperature
Configuration | Turbine Load | 10oF | 59 oF | 102 oF
Turbine Startup | Startup | 101.32 | 87.08 | 92.82
Turbine + Duct Firing | 100% | 90.1 | 86.2 | 82.8
Turbine | 100% | 56.5 | 52.6 | 49.2
Turbine | 80% | 47.1 | 43.5 | 38.9
Turbine | Minimum Compliance Load | 41 | 33.3 | 33.3
NOx (controlled) |  | lb/hour
Ambient Temperature
Configuration | Turbine Load | 10oF | 59 oF | 102 oF
Turbine Startup Average (No Control) | Startup | 101.32 | 87.08 | 92.82
Turbine + Duct Firing | 100% | 15.6 | 14.7 | 14 | Maximum Normal Operation = | 15.6 | lb/hour | controlled
Turbine | 100% | 12.6 | 11.7 | 10.9
Turbine | 80% | 10.5 | 9.7 | 8.6
Turbine | Minimum Compliance Load | 9.1 | 7.4 | 7.4
CO (uncontrolled) |  | lb/hour
Ambient Temperature
Configuration | Turbine Load | 10oF | 59 oF | 102 oF
Turbine Startup Average (No Control) | Startup | 262.28 | 243.32 | 240.28
Turbine + Duct Firing | 100% | 69.8 | 67.6 | 65.8
Turbine | 100% | 27.8 | 25.6 | 23.8
Turbine | 80% | 23 | 21.2 | 19.1
Turbine | Minimum Compliance Load | 20 | 17.1 | 17.4
CO (controlled) |  | lb/hour
Ambient Temperature
Configuration | Turbine Load | 10oF | 59 oF | 102 oF
Turbine Startup (No control) | Startup | 262.28 | 243.32 | 240.28
Turbine + Duct Firing | 100% | 9.5 | 9 | 8.5 | Maximum Normal Operation = | 9.5 | lb/hour | controlled
Turbine | 100% | 7.6 | 7.1 | 6.7
Turbine | 80% | 6.4 | 5.9 | 5.3
Turbine | Minimum Compliance Load | 5.5 | 4.5 | 4.5
VOC (uncontrolled) |  | lb/hour
Ambient Temperature
Configuration | Turbine Load | 10oF | 59 oF | 102 oF
Turbine Startup Average (No Control) | Startup | 17.56 | 16.76 | 16.06
Turbine + Duct Firing | 100% | 6.9 | 6.7 | 6.6
Turbine | 100% | 2.7 | 2.5 | 2.4
Turbine | 80% | 2.2 | 2.1 | 1.9
Turbine | Minimum Compliance Load | 1.9 | 1.7 | 1.7
VOC (controlled) |  | lb/hour
Ambient Temperature
Configuration | Turbine Load | 10oF | 59 oF | 102 oF
Turbine Startup (No control) | Startup | 17.56 | 16.76 | 16.06
Turbine + Duct Firing | 100% | 4.1 | 4 | 3.8 | Maximum Normal Operation = | 4.1 | lb/hour | controlled
Turbine | 100% | 1.593 | 1.475 | 1.416
Turbine | 80% | 1.298 | 1.239 | 1.121
Turbine | Minimum Compliance Load | 1.121 | 1.003 | 1.003
SO2 |  | lb/hour
Ambient Temperature
Configuration | Turbine Load | 10oF | 59 oF | 102 oF
Turbine Startup | Startup | 3.6 | 3.4 | 3.2 | Maximum Normal Operation = | 4.1 | lb/hour
Turbine + Duct Firing | 100% | 4.1 | 3.8 | 3.6
Turbine | 100% | 3.6 | 3.4 | 3.2
Turbine | 80% | 3 | 2.8 | 2.5
Turbine | Minimum Compliance Load | 2.6 | 2.1 | 2.1
PM/PM10/PM2.5 |  | lb/hour
Ambient Temperature
Configuration | Turbine Load | 10oF | 59 oF | 102 oF
Turbine Startup | Startup | 6.5 | 6.5 | 6.5
Turbine + Duct Firing | 100% | 8.5 | 8.5 | 8.5 | Maximum Normal Operation = | 8.5 | lb/hour
Turbine | 100% | 6.5 | 6.5 | 6.5
Turbine | 80% | 6.5 | 6.5 | 6.5
Turbine | Minimum Compliance Load | 6.5 | 6.5 | 6.5
Startup emissions are the maximum emissions for each ambient temperature from spreadsheet titled "Turbine Startup Data & Emissions". For SO2 and PM/PM10/PM2.5 maximum normal operation emission rate is used for startup Turbine normal operation emissions are from heat balance provided by Kiewit Power Engineers. Heat balance shows no control for VOCs with no duct firing. Control efficiency of 41.0% from heat balance for VOC emissions with duct firing used to calculate controlled VOC emissions for normal operation with no duct firing. Controlled VOC Emissions (no duct firing) lb = Uncontrolled VOC Emissions (no duct firing) lb x (1 - Control Efficiency [0.41]) hour hour

## Turbine and Duct Burner Annual
BOWIE POWER STATION COMBINED TURBINE AND DUCT BURNER ANNUAL EMISSIONS
Duct Burner Hours of Operation for capacity factor assuming 100% load = |  |  |  | 4224 | hours/year
Hours in Shutdown = |  |  |  | 91.25 | hours/year
Turbine Capacity Factor = |  |  |  | 95%
Hours of Turbine Operation (no duct firing) per Year = |  |  |  | 3681.75 | hours/year
Startup Hours = |  |  |  | 325 | hours/year
|  |  | TOTAL | 8322 | hours/year
NOx Emissions (uncontrolled) |  | tons/year
Startup Emissions |  | 14.1505
Turbine + Duct Firing |  | 182.0544
Turbine |  | 96.83
Shutdown |  | 6.5518
| Total | 299.5867
NOx Emissions (Controlled) |  | tons/year
Startup Emissions (partial control) |  | 14.1505
Turbine + Duct Firing |  | 31.0464
Turbine |  | 21.5382
Shutdown |  | 2.732
| Total | 69.4672
CO Emissions (uncontrolled) |  | tons/year
Startup Emissions |  | 39.5395
Turbine + Duct Firing |  | 142.7712
Turbine |  | 47.1264
Shutdown |  | 19.199
| Total | 248.6361
CO Emissions (controlled) |  | tons/year
Startup Emissions (partial control) |  | 39.5395
Turbine + Duct Firing |  | 19.008
Turbine |  | 13.0702
Shutdown |  | 8.9243
| Total | 80.542
VOC Emissions (uncontrolled) |  | tons/year
Startup Emissions |  | 2.7235
Turbine + Duct Firing |  | 14.1504
Turbine |  | 4.6022
Shutdown |  | 1.0841
| Total | 22.5601
VOC Emissions (controlled) |  | tons/year
Startup Emissions (partial control) |  | 2.7235
Turbine + Duct Firing |  | 8.448
Turbine |  | 2.7153
Shutdown |  | 1.0841
| Total | 14.9708
SO2 Emissions |  | tons/year
Startup Emissions |  | 0.5525
Turbine + Duct Firing |  | 8.0256
Turbine |  | 6.259
Shutdown |  | 0.16425
| Total | 15.0013
PM/PM10/PM2.5 Emissions |  | tons/year
Startup Emissions |  | 1.0562
Turbine + Duct Firing |  | 17.952
Turbine |  | 11.9657
Shutdown |  | 0.29656
| Total | 31.2705
Hours of Turbine only Operation: Turbine Only Operation hours = (8760 hours x capacity factor) - duct burner operation hours - startup hours - shutdown hours year year year year year Startup and Normal Operation lb/hour emission values used in calculations for all pollutants are from the spreadsheet "Turbine and Duct Burner Hourly". Emissions are calculated based on the annual average ambient temperature of 59oF. Shutdown emission values are from the spreadsheet "Turbine Shutdown Emissions". tons = lb x hours x tons year hour year 2000 lb

## Turbine Startup Emissions
BOWIE POWER STATION TURBINE STARTUP EMISSIONS
| Number Per Turbine | Duration (minutes) | Duration (hours)
Hot Starts - <8 hours shutdown | 80 | 30 | 0.5
Warm Starts - 8 to 72 hours shutdown | 220 | 60 | 1
Cold Starts - >72 hours shutdown | 65 | 60 | 1
Total Hours in Startup/Year | 325 | per turbine
The following uncontrolled emission rates are from spreadsheet: "Bowie_7FA04_Cycle_Emissions_Fill_in_Table Kiewit Revisions 6-19-13", Kiewit Power Engineers CO.
Emission Rates - Hot Starts (lb/event/turbine) |  |  |  | Emission Rates - Hot Starts (lb/hour/turbine)
| Ambient Temperature |  |  |  | Ambient Temperature
Pollutant | 10oF | 59 oF | 102 oF | Pollutant | 10oF | 59 oF | 102 oF
NOx | 50.66 | 43.54 | 46.41 | NOx | 101.32 | 87.08 | 92.82
CO | 131.14 | 121.66 | 120.14 | CO | 262.28 | 243.32 | 240.28
VOC | 8.78 | 8.38 | 8.03 | VOC | 17.56 | 16.76 | 16.06
Emission Rates - Warm Starts (lb/hour/turbine)a
Ambient Temperature
Pollutant | 10oF | 59 oF | 102 oF
NOx | 78.91 | 69.86 | 71.03
CO | 145.03 | 134.46 | 132.03
VOC | 10.12 | 9.63 | 9.21
Emission Rates - Cold Starts (lb/hour/turbine)a
Ambient Temperature
Pollutant | 10oF | 59 oF | 102 oF
NOx | 78.91 | 69.86 | 71.03
CO | 145.03 | 134.46 | 132.03
VOC | 10.12 | 9.63 | 9.21
aAs warm and cold starts last 60 minutes, lb/hour emissions and emissions on a lb/event/basis are equivalent.
Total Hours in Startup = (Number of Hot Start x Hours ) + (Number of Warm Starts x Hours ) + (Number of Cold Starts x Hours ) Year Year Hot Start Year Warm Start Year Cold Start Hot Start lb = lb x event hour event hour

## Turbine Shutdown Emissions
BOWIE POWER STATION TURBINE SHUTDOWN EMISSIONS
Shutdowns per year | 365 | shutdowns/year
Shutdown Duration | 0.25 | hours/shutdown
Hours in Shutdown | 91.25 | hours shutdown/year
Pollutant | Shutdown Uncontrolled Emissions Per Turbine (lbs/shutdown) |  |  |  | Pollutant | Shutdown Uncontrolled Emissions Per Turbine (lbs/shutdown)
Ambient Temperature | 10oF | 59 oF | 102 oF |  | Ambient Temperature | 10oF | 59 oF | 102 oF
Controllable NOxa | 33.53 | 26.9 | 30.2 |  | NOxa | 42.53 | 35.9 | 39.2
Uncontrollable NOxa | 9 | 9 | 9 |  | COa | 114.41 | 105.2 | 103.91
Controllable COa | 87.41 | 78.2 | 76.91 |  | VOC | 6.43 | 5.94 | 5.68
Uncontrollable COa | 27 | 27 | 27
Pollutant | Shutdown Controlled Emissions Per Turbine (lbs/shutdown)a
Ambient Temperature | 10oF | 59 oF | 102 oF
NOxa | 16.44 | 14.97 | 15.7
COa | 51.47 | 48.9 | 48.53
VOCb | 6.43 | 5.94 | 5.68
aEmissions from spreadsheet: "SUSD Emissions", Kiewit Power Engineers CO. Controllable emissions are those that occur from minimum compliance load to full speed no load. Uncontrollable emissions are those that occur from full speed no load to flameout.
bEmissions from spreadsheet: "Bowie_7FA04_Cycle_Emissions_Fill_in_Table Kiewit Revisions 6-19-13", Kiewit Power Engineers CO. Controlled VOC emissions are not available, conservatively assume VOC shutdown emissions are uncontrolled.
Annual Shutdown Emissions
| Uncontrolled (tons/year) | Controlled (tons/year)
NOx | 6.5518 | 2.732
CO | 19.199 | 8.9243
VOC | 1.0841 | 1.0841
For modeling purposes determine maximum emissions in an hour
Calculate emissions for an hour during which a shutdown event occurs. Maximum emissions would occur when emissions during the hour were from normal operation followed by emissions from a shutdown event.
| Normal Operation Controlled Emissions Each Turbine (lb/hour)c |  |  | Total Controlled Emissions with Normal Operations Followed by Turbine Shutdown (lbs in one hour) |  |  | Maximum Emissions for Hour with Shutdown (lb/hour) |  | Maximum Emissions for Hour with a Startup (lb/hour) | Maximum Normal Operations Emissions (lb/hour) | Condition for Hour with Maximum Emissions
| 10oF | 59 oF | 102 oF | 10oF | 59 oF | 102 oF
NOx | 15.6 | 14.7 | 14 | 28.14 | 25.995 | 26.2 | 28.14 |  | 101.32 | 15.6 | Startup
CO | 9.5 | 9 | 8.5 | 58.595 | 55.65 | 54.905 | 58.595 |  | 262.28 | 9.5 | Startup
VOC | 4.1 | 4 | 3.8 | 9.505 | 8.94 | 8.53 | 9.505 |  | 17.56 | 9.5 | Startup
cNormal operation emissions includes duct burner emissions.
hours in shutdown hours = shutdowns x hours . year year shutdown NOx and CO Uncontrolled Shutdown Emissions lb = Controllable Portion of Shutdown Emissions lb + Uncontrolled Shutdown Emissions lb . shutdown shutdown shutdown Annual Shutdown Emissions tons = Emissions for Shutdown Hour @ 59oF lb x shutdown s x tons . year shutdown year 2000 lbs Emissions from an hour with normal operations followed by a shutdown event = ( lb controlled normal operation x portion of hour normal operation) + lbs uncontrolled from shutdown hour = ( lb controlled normal operation x (1 - portion of hour in shutdown)) + lbs uncontrolled from shutdown hour Maximum hourly emissions for startup are from "Turbine Startup Emissions" spreadsheet Maximum hourly emissions for normal operation are from "Turbine and Duct Burner Hourly" spreadsheet

## Turbine and DB Heat Input
BOWIE POWER STATION TURBINE AND DUCT BURNER HEAT INPUTS
Heat Input, mmBtu/hour HHV - Total Two Turbines
Ambient Temperature | 10 oF | 59 oF | 102 oF
Turbine + Duct Firing | 3469.12 | 3231.74 | 3023.86
Turbine 100% | 3469.12 | 3231.74 | 3023.86
Turbine 80% | 2895.28 | 2670.88 | 2386.46
Turbine Minimum Compliance Load | 2516.42 | 2041.6 | 2041.62
Heat Input, mmBtu/hour HHV - Each Turbine
Ambient Temperature | 10 oF | 59 oF | 102 oF
Turbine + Duct Firing | 1734.56 | 1615.87 | 1511.93
Turbine 100% | 1734.56 | 1615.87 | 1511.93
Turbine 80% | 1447.64 | 1335.44 | 1193.23
Turbine Minimum Compliance Load | 1258.21 | 1020.8 | 1020.81
Turbine Maximum Heat Input Rate
mmBtu per hour (HHV) | gigaJoules per hour (HHV)
1734.56 | 1829.6139
Maximum Turbine Annual Heat Input
Capacity Factor |  |  | 95%
Annual Turbine Heat Input (mmBtu/year) |  |  | 14435008.32
Annual Turbine Heat Input Both Turbines (mmBtu/year) |  |  | 28870016.64
Duct Burner Maximum Fuel Use
Duct Burner Heat Input Rate (mmBtu/hour) (HHV) |  |  | 420
Duct Burner Hours of Operation at Full Load (hours/year) |  |  | 4224
Annual Duct Burner Heat Input (mmBtu/year) |  |  | 1774080
Annual Duct Burner Heat Input Both Duct Burners (mmBtu/year) |  |  | 3548160
gigaJoules = mmBtu x 106 Btu x 1054.8 Joule x gigaJoule hour hour mmBtu Btu 109 Joule Turbine Annual Heat Input mmBtu = Maximum Heat Input mmBtu (HHV) x 8760 hours x Capacity Factor year hour year Duct Burner Annual Heat Input mmBtu = Heat Input mmBtu x hours year hour year

## Turbine HAP Emissions
BOWIE POWER STATION TURBINE HAP EMISSIONS
| per turbine |  | two turbines
Turbine Heat Input (HHV) = | 1734.56 | mmBtu/hour | 3469.12 | mmBtu/hour
Annual Heat Input (HHV)= | 14435008.32 | mmBtu/year | 28870016.64 | mmBtu/year
Natural Gas Heat Content |  | 1034.6
Oxidation Catalyst Control Efficiency = |  | 70%
Oxidation Catalyst Control Efficiency During Startup = |  | 0% | Conservatively assume no HAP control during startup or shutdown
Total Hours per Year in Operation = |  | 8322
Hours per Year in Startup = |  | 325
Hours per Year in Shutdown = |  | 91.25
Operating Hours per Year in Startup or Shutdown = |  | 416.25
Operating Hours per Year Not in Startup = |  | 7997
Hazardous Air Pollutant | AP-42 Table 3.1-3 Emission Factor (lb/mmBtu)a | Emission Factor Adjusted for Natural Gas Heat Content (lb/mmBtu) | Uncontrolled Hourly Emissions for One Turbine (lb/hr) | Controlled Annual Emissions for One Turbine (tons per year)
Acetaldehyde | 4e-05 | 4.0573e-05 | 0.070376 | 0.099066
Acrolein | 6.4e-06 | 6.4916e-06 | 0.01126 | 0.015851
Benzene | 1.2e-05 | 1.2172e-05 | 0.021113 | 0.02972
Ethylbenzene | 3.2e-05 | 3.2458e-05 | 0.0563 | 0.079253
Formaldehyde | 0.00071 | 0.00072016 | 1.2492 | 1.7584
Naphthalene | 1.3e-06 | 1.3186e-06 | 0.0022872 | 0.0032196
PAHs | 2.2e-06 | 2.2315e-06 | 0.0038707 | 0.0054486
Toluene | 0.00013 | 0.00013186 | 0.22872 | 0.32196
Xylenes (mixed) | 6.4e-05 | 6.4916e-05 | 0.1126 | 0.15851
aEmission factors are from AP-42, Section 3.1, Table 3.1-3, April 2000. Pollutants for which AP-42 records one half the source testing detection limit have not been included.
Conservatively assume maximum heat input during all operating hours: mmBtu = mmBtu x 8760 hours x capacity factor year hour year AP-42 Emission Factor Adjustment for Natural Gas Heat Content from footnote c, Table 3.1-3: Adjusted Emission Factor lb = AP-42 Emission Factor lb x Heat Content Bowie Natural Gas (Btu/scf) mmBtu mmBtu 1020 Btu/scf lb/hour uncontrolled lb = lb x mmBtu hour mmBtu hour tons/year controlled tons = (( lb x hours of Operation Not in Startup x (1 - Control Efficiency)) + ( lb x hours in Startup)) x tons . year hour year hour year 2000 lb

## Duct Burner HAP Emissions
BOWIE POWER STATION DUCT BURNER HAP EMISSIONS
Natural Gas Heat Content | 1034.6 | Btu/scf
Duct Burner Heat Input (HHV) = | 420 | MMBtu/hour
| 1774080 | MMBtu/year | each duct burner
| 3548160 | MMBtu/year | combined for two duct burners
Oxidation Catalyst Control Efficiency = | 70%
Hazardous Air Pollutant | Emission Factor lb/million scf | Emission Factor (lb/MMBtu)1 | Uncontrolled Hourly Emissions for One Duct Burner (lb/hour) | Controlled Annual Emissions for One Duct Burner (tons/year)2
Arsenic | 0.0002 | 1.9331e-07 | 8.1191e-05 | 0.00017147
Benzene | 0.0021 | 2.0298e-06 | 0.0008525 | 0.00054015
Cadmium | 0.0011 | 1.0632e-06 | 0.00044655 | 0.00094311
Chromium | 0.0014 | 1.3532e-06 | 0.00056834 | 0.0012003
Cobalt | 8.4e-05 | 8.1191e-08 | 3.41e-05 | 7.2019e-05
Dichlorobenzene | 0.0012 | 1.1599e-06 | 0.00048714 | 0.00030865
Formaldehyde | 0.075 | 7.2492e-05 | 0.030447 | 0.019291
Hexane | 1.8 | 0.0017398 | 0.73072 | 0.46298
Lead | 0.0005 | 4.8328e-07 | 0.00020298 | 0.00042869
Manganese | 0.00038 | 3.6729e-07 | 0.00015426 | 0.0003258
Mercury | 0.00026 | 2.513e-07 | 0.00010555 | 0.00022292
Naphthalene | 0.00061 | 5.896e-07 | 0.00024763 | 0.0001569
Nickel | 0.0021 | 2.0298e-06 | 0.0008525 | 0.0018005
POM | 5.18e-05 | 5.0068e-08 | 2.1028e-05 | 1.3324e-05
Toluene | 0.0034 | 3.2863e-06 | 0.0013802 | 0.00087452
POM | lb/million scf
2-Methylnaphthalene | 2.4e-05
Fluoranthene | 3e-06
Fluorene | 2.8e-06
Phenanathrene | 1.7e-05
Pyrene | 5e-06
Total POM | 5.18e-05
1Emission factors are from AP-42 Section 1.4 "Natural Gas Combustion", Tables 1.4-2 (lead),-3 (organics), and -4 (metals), July 1998
2Organic pollutant emissions are controlled by the oxidation catalysts. Lead and metal pollutant emissions (arsenic, cadmium, chromium, cobalt, lead, manganese, mercury, and nickel) are uncontrolled.
mmBtu = mmBtu x hours year hour year lb = lb x scf . mmBtu million scf Btu Uncontrolled Hourly Emissions lb = lb x mmBtu hour mmBtu hour Metal HAPs - uncontrolled tons = lb x mmBtu x tons . year mmBtu year 2000 lb Organic HAPs - controlled tons = lb x mmBtu x tons x (1 - control efficiency) year mmBtu year 2000 lb

## Turbine+Duct Burner HAPs
BOWIE POWER STATOIN TURBINE AND DUCT BURNER HAP EMISSIONS
Turbine and duct burner lb/hour emission values are needed to complete the application forms.
Oxidation catalysts provide control for only a portion of each startup sequence. It has been assumed that shutdown emissions are uncontrolled. As a conservative assumption, turbine uncontrolled emissions will be reviewed.
The duct burners do not operate during startup.
During Normal Operation, HAPs will be emitted from both the turbine and duct burner and will be controlled by the oxidation catalyst
For organic HAP hourly emissions, determine whether turbine emissions during startup/shutdown or turbine and duct burner emissions during normal operations are greater.
All values shown below are for one turbine and duct burner pair.
Oxidation Catalyst Control Efficiency |  | 70%
Pollutant | Turbine Uncontrolled Emissions During Startup (lb/hour) | Duct Burner Uncontrolled Emissions (lb/hour) | Turbine + Duct Burner Controlled Emissions during normal operations (lb/hour) | Turbine + Duct Burner Maximum Short-Term Emissions (lb/hour)
Acetaldehyde | 0.070376 |  | 0.021113 | 0.070376
Acrolein | 0.01126 |  | 0.003378 | 0.01126
Benzene | 0.021113 | 0.0008525 | 0.0065895 | 0.021113
Dichlorobenzene |  | 0.00048714 | 0.00014614 | 0.00014614
Ethylbenzene | 0.0563 |  | 0.01689 | 0.0563
Formaldehyde | 1.2492 | 0.030447 | 0.38388 | 1.2492
Hexane |  | 0.73072 | 0.21922 | 0.21922
Naphthalene | 0.0022872 | 0.00024763 | 0.00076045 | 0.0022872
POMsa | 0.0038707 | 2.1028e-05 | 0.0011675 | 0.0038707
Toluene | 0.22872 | 0.0013802 | 0.06903 | 0.22872
Xylenes | 0.1126 |  | 0.03378 | 0.1126
aPAHs are a subset of POMs.
Summarize Turbine and Duct Burner HAP Emission:
Pollutant | Turbine + Duct Burner Emissions (lb/hour)b | Turbine Emissions (tons/year) | Duct Burner Emissions (tons/year) | Turbine + Duct Burner Emissions (tons/year)
Acetaldehyde | 0.070376 | 0.099066 |  | 0.099066
Acrolein | 0.01126 | 0.015851 |  | 0.015851
Arsenic | 8.1191e-05 |  | 0.00017147 | 0.00017147
Benzene | 0.021113 | 0.02972 | 0.00054015 | 0.03026
Cadmium | 0.00044655 |  | 0.00094311 | 0.00094311
Chromium | 0.00056834 |  | 0.0012003 | 0.0012003
Cobalt | 3.41e-05 |  | 7.2019e-05 | 7.2019e-05
Dichlorobenzene | 0.00014614 |  | 0.00030865 | 0.00030865
Ethylbenzene | 0.0563 | 0.079253 |  | 0.079253
Formaldehyde | 1.2492 | 1.7584 | 0.019291 | 1.7777
Hexane | 0.21922 |  | 0.46298 | 0.46298
Lead | 0.00020298 |  | 0.00042869 | 0.00042869
Manganese | 0.00015426 |  | 0.0003258 | 0.0003258
Mercury | 0.00010555 |  | 0.00022292 | 0.00022292
Naphthalene | 0.0022872 | 0.0032196 | 0.0001569 | 0.0033765
Nickel | 0.0008525 |  | 0.0018005 | 0.0018005
POMsa | 0.0038707 | 0.0054486 | 1.3324e-05 | 0.0054619
Toluene | 0.22872 | 0.32196 | 0.00087452 | 0.32284
Xylenes | 0.1126 | 0.15851 |  | 0.15851
aPAHs are a subset of POMs.
bOrganic HAP Emissions are maximums from table above. Metal HAPs (arsenic, cadmium, chromium, cobalt, lead, manganese, mercury, and nickel) are from "Duct Burner HAP Emissions".
Turbine Emissions are from "Turbine HAP Emissions" spreadsheet. Duct Burner emissions are from "Duct Burner HAP Emissions" Controlled Emissions lb = (Turbine Emissions lb + Duct Burner Emissions lb ) x (1 - Control Efficiency) hour hour hour

## Aux Boiler Emissions
BOWIE POWER STATION AUXILIARY BOILER DATA AND EMISSIONS
Stack Parameters
Stack Height | 13.7 | meters
| 44.9497 | feet
Stack Temperature | 300 | oF | From Rentech Data sheet
| 422.0389 | K
Stack Exit Velocity | 50 | feet/second | From Rentech Data sheet
| 15.2393 | meters/second
Stack Diameter | 30 | inches | From Rentech Data sheet
| 2.5 | feet
| 0.76196 | meters
Operating Data
Heat Input Rating | 50 | MMBtu/hr
Operating Hours | 450 | hrs/yr
Natural Gas Heat Content | 1034.6 | Btu/scf
Natural Gas Sulfur Content | 0.75 | grains/100 scf
| 7500 | grains/106 scf
Fuel Consumption Rate | 0.048328 | mmscf/hr
Annual Fuel Usage | 21.7475 | mmscf/yr
Criteria Pollutant Emission Estimation
Pollutant | Emission Factor (lb/mmscf) | Adjusted Emission Factor (lb/mmscf) | Emission Factor (lb/mmBtu) | Reference | Hourly Emissions (lb/hour) | Annual Emissions (tpy)
NOx |  |  | 0.011 | Rentech Data Sheet | 0.55 | 0.12375
CO |  |  | 0.037 | Rentech Data Sheet | 1.85 | 0.41625
VOC |  |  | 0.004 | Rentech Data Sheet | 0.2 | 0.045
SOx | 0.6 | 2.25 |  | AP-42, Table 1.4-2, 7/98 | 0.10874 | 0.024466
PM |  |  | 0.007 | Rentech Data Sheet | 0.35 | 0.07875
PM10 |  |  | 0.007 | Rentech Data Sheet | 0.35 | 0.07875
Hazardous Air Pollutant Emission Estimation
Pollutant | Emission Factor (lb/mmscf) | Emission Factor Reference | Hourly Emissions (lb/hour) | Annual Emissions (tpy)
Arsenic | 0.0002 | AP-42, Table 1.4-4, 7/98 | 9.6656e-06 | 2.1748e-06
Benzene | 0.0021 | AP-42, Table 1.4-3, 7/98 | 0.00010149 | 2.2835e-05
Cadmium | 0.0011 | AP-42, Table 1.4-4, 7/98 | 5.3161e-05 | 1.1961e-05
Chromium | 0.0014 | AP-42, Table 1.4-4, 7/98 | 6.7659e-05 | 1.5223e-05
Cobalt | 8.4e-05 | AP-42, Table 1.4-4, 7/98 | 4.0595e-06 | 9.134e-07
Dichlorobenzene | 0.0012 | AP-42, Table 1.4-3, 7/98 | 5.7993e-05 | 1.3049e-05
Formaldehyde | 0.075 | AP-42, Table 1.4-3, 7/98 | 0.0036246 | 0.00081553
Hexane | 1.8 | AP-42, Table 1.4-3, 7/98 | 0.08699 | 0.019573
Lead | 0.0005 | AP-42, Table 1.4-2, 7/98 | 2.4164e-05 | 5.4369e-06
Manganese | 0.00038 | AP-42, Table 1.4-4, 7/98 | 1.8365e-05 | 4.132e-06
Mercury | 0.00026 | AP-42, Table 1.4-4, 7/98 | 1.2565e-05 | 2.8272e-06
Naphthalene | 0.00061 | AP-42, Table 1.4-3, 7/98 | 2.948e-05 | 6.633e-06
Nickel | 0.0021 | AP-42, Table 1.4-4, 7/98 | 0.00010149 | 2.2835e-05
POM | 5.18e-05 |  | 2.5034e-06 | 5.6326e-07
Toluene | 0.0034 | AP-42, Table 1.4-3, 7/98 | 0.00016431 | 3.6971e-05
POM
2-Methylnaphthalene | 2.4e-05 | AP-42, Table 1.4-3, 7/98
Fluoranthene | 3e-06 | AP-42, Table 1.4-3, 7/98
Fluorene | 2.8e-06 | AP-42, Table 1.4-3, 7/98
Phenanathrene | 1.7e-05 | AP-42, Table 1.4-3, 7/98
Pyrene | 5e-06 | AP-42, Table 1.4-3, 7/98
Total POM | 5.18e-05
feet = meters x 3.281 feet . meters K = [5 (oF-32)] + 273.15 9 meters = feet x meters . second second 3.281 feet feet = inches x feet . 12 inches meters = inches x feet x meters . 12 inches 3.281 feet grains = grains x 1,000,000 scf 106 scf 100 scf 106 scf mmscf = mmBtu x 1,000,000 Btu x scf x mmscf . hour hour mmBtu Btu 1,000,000 scf mmscf = mmscf x hours year hour year Adjust AP-42, SO2 emission factor for heat and sulfur content of Bowie natural gas: Adjusted Emission Factor lb = lb x Bowie Sulfur Content grains/scf . mmscf mmscf AP-42 Sulfur Content 2,000 grains/scf lb/hour emissions: lb = lb x mmBtu hour mmBtu hour lb = lb x mmscf hour mmscf hour tons = lb x mmBtu x hours x tons . year mmBtu hour year 2000 lb tons = lb x mmscf x tons . year mmscf year 2000 lb

## Emergency Fire Pump Emissions
BOWIE POWER STATION EMERGENCY FIRE PUMP DATA AND EMISSIONS
Cummins CFP9E-F10 Fire Power engine
Stack Parameters
Stack Height | 35 | feet
| 10.6675 | meters
Stack Temperature | 997 | oF | From Cummins sheet
| 809.2611 | K
Stack Exit Flowrate | 1751 | cubic ft/minute | From Cummins sheet
Stack Exit Velocity | 12841.5885 | feet/minute
| 214.0265 | feet/second
| 65.2321 | meters/second
Stack Diameter | 5 | inches
| 0.41667 | feet
| 0.12699 | meters
Operating Data
Engine Rating | 260 | hp
Operating Hours | 100 | hrs/yr | Hours limit from 40 CFR 60.4211(e)
Fuel Consumption Rate | 13.4 | gal/hr | Manufacturer's Data
Diesel Heat Content | 137000 | Btu/gal | Diesel BTU content from AP-42, Appendix A, Page A-5
Hourly Heat Input | 1.8358 | mmBtu/hour
Annual Fuel Usage | 1.34 | thousand gal/year
Diesel Sulfur Content | 15 | ppm | Diesel sulfur content required by 40 CFR Subpart IIII 60.4207(b) which refers to 80.510(b)
| 0.0015 | %
Criteria Pollutant Emission Estimation - one fire pump
Pollutant | Emission Factor (lb/hp hr) | Emission Factor (lb/hp hr) | Emission Factor (g/hp hr) | Emission Factor Reference | Hourly Emissions (lb/hour) | Annual Emissions (tpy)
NOx |  |  | 2.2 | Manufacturer | 1.2611 | 0.063053
CO |  |  | 1.417 | Manufacturer | 0.81223 | 0.040612
VOC |  |  | 0.123 | Manufacturer | 0.070504 | 0.0035252
SOx | 8.09E-03 * sulfur content % | 1.2135e-05 |  | AP-42, 10/96, Table 3.4-1a | 0.0031551 | 0.00015776
PM |  |  | 0.118 | Manufacturer | 0.067638 | 0.0033819
PM10 |  |  | 0.118 | Assume PM10 = PM | 0.067638 | 0.0033819
aAP-42 Section 3.3, "Gasoline and Diesel Industrial Engines" indicates that SO2 emissions are directly related to fuel sulfur content. However, the emission factors provided in that section do not include a factor for fuel sulfur content nor is the fuel sulfur content related to the factors provided. AP-42 Section 3.4, "Large Stationary Diesel and All Stationary Dual-fuel Engines" includes SO2 emissions factors that take fuel sulfur content into account and that assume that all sulfur in fuel is converted to SO2. To ensure that the fuel sulfur content is taken into consideration, the emission factor from section 3.4-1 has been used.
HAP Emission Estimation
HAP | Emission Factor (lb/mmBtu) | Emission Factor (lb/thousand Gallons) | Emission Factor Reference | Hourly Emissions (lb/hour) | Annual Emissions (tpy)
Acetaldehyde | 0.000767 |  | AP-42, 10/96, Table 3.3-2 | 0.0014081 | 7.0403e-05
Benzene | 0.000933 |  | AP-42, 10/96, Table 3.3-2 | 0.0017128 | 8.564e-05
Ethylbenzene |  | 0.00307 | WebFIRE SCC 20100102 | 4.1138e-05 | 2.0569e-06
Formaldehyde | 0.00118 |  | AP-42, 10/96, Table 3.3-2 | 0.0021662 | 0.00010831
Naphthalene | 8.48e-05 |  | AP-42, 10/96, Table 3.3-2 | 0.00015568 | 7.7838e-06
PAHs (total) | 0.000168 |  | AP-42, 10/96, Table 3.3-2 | 0.00030841 | 1.5421e-05
Toluene | 0.000409 |  | AP-42, 10/96, Table 3.3-2 | 0.00075084 | 3.7542e-05
Xylene | 0.000285 |  | AP-42, 10/96, Table 3.3-2 | 0.0005232 | 2.616e-05
meters = feet x meters 3.281 feet K = [5 (oF-32)] + 273.15 9 Exit Velocity ft = Flowrate (ft3/min) = Flowrate (ft3/min) = Flowrate (ft3/min) . min Area (ft2) π x (diameter [ft])2 π x (diameter [inches] x ft/12 inches)2 2 2 ft = ft x min . sec min 60 sec meters = ft x minute x meters . second min 60 seconds 3.281 feet feet = inches x feet . 12 inches meters = inches x feet x meters 12 inches 3.281 feet Heat Input Rate is calculated as follows: mmBtu = gallons x Btu x mmBtu . hour hour gallon 1,000,000 Btu Annual Fuel Usage is calculated as follows: thousand gallons = gallons x operational hours x thousand gallons year hour year 1,000 gallons
% Sulfur in Diesel Fuel is Calculated as follows: % = parts x 100 1,000, 000 Short-Term Emissions in lb per hour are calculated as follows: lb = grams x hp x lb . hour hp hr 453.59 grams lb = lb x hp hour hp hr lb = emission factor lb x mmBtu . hour mmBtu hour lb = emission factor lb x gallons x thousand gallons hour thousand gallons hour 1,000 gallons Annual Emissions in tons per year are calculated as follows: tons = grams x hp x lb x hours x tons . year hp hr 453.59 grams year 2000 lb tons = lbs x hp x hours x tons . year hp hr year 2000 lb tons = emission factor lb x mmBtu x hours x tons . year mmBtu hour year 2000 lb tons = emission factor lb x thousand gallons x tons . year thousand gallons year 2000 lb

## Cooling Tower
BOWIE POWER STATION COOLING TOWER PM/PM10/PM2.5 EMISSIONS
Stack Parameters
Stack Height | 14 | meters
| 45.934 | feet
Stack Temperature | 70 | oF
| 294.2611 | K
Stack Exit Flowrate per Cell | 1430000 | ft3/minute
| 674.974 | meters3/second
Stack Exit Velocity per Cell | 8.594 | meters/second
| 28.197 | ft/second
Stack Diameter per Cell | 10 | meters
| 32.81 | feet
Cooling Tower Data
towers | 1
cells/tower | 9
ppm by weight TDS in blowdown | 4039 | ppmw
Drift | 0.0005%
Flowrate | 127860 | gallons/minute
Capacity Factor | 100%
Cooling Tower Emissions
PARTICULATE MATTER
TDS in Blowdown (ppmw) | 4039 | ppmw
TDS in blowdown (mg/l) [ppmw approximately = mg/l] | 4039 | mg/l
Flow of dissolved solids (lbs/gallon) | 0.033748 | lbs/gallon
Flowrate of tower (gallons per minute) | 127860 | gallons/minute
Drift % | 0.0005%
Peak Drift (gallons/minute) | 0.6393 | gallons/minute
Pollutant | % of PMa | Hourly Emissions (lb/hour) | Annual Emissions (tpy)
PM |  | 1.2945 | 5.67
PM10 | 67.4669 | 0.87337 | 3.8253
PM2.5 | 32.1522 | 0.41621 | 1.823
aCalculated on page 3.
Particle Size Distribution
TDS in blowdown |  | 4039 | ppmw
Droplet Diameter (μm)a | % Mass Largera | % Mass Smaller | Solid Particle Diameter (μm)
525 | 0.2 | 99.8 | 64.285
375 | 1 | 99 | 45.9179
230 | 5 | 95 | 28.163
170 | 10 | 90 | 20.8161
115 | 20 | 80 | 14.0815
65 | 40 | 60 | 7.9591
35 | 60 | 40 | 4.2857
15 | 80 | 20 | 1.8367
10 | 88 | 12 | 1.2245
81.6676 | 32.5331 | 67.4669 | 10
20.4169 | 67.8478 | 32.1522 | 2.5
aFrom "Cooling Tower Drift Mass Distribution, Excel Drift Eliminators" for Marley TU10 and TU12 drift eliminators
feet = meters x 3.281 feet meters K = [5 (oF-32)] + 273.15 9 cubic meters = cubic feet x cubic meters x minute . second minute 35.31 cubic feet 60 seconds Flowrate = Exit Velocity x Area Exit velocity ( meters ) = Flowrate (cubic meters/second) . second PI x (stack diameter (meters)/2)2 feet = meters x 3.281 feet second second meter For water ppm = mg/liter lb/gallon is calculated as follows: lb = mg x 3.79 liters x grams x lb . gallon liter gallons 1000 mg 453.69 grams Peak drift in gallons/minute is calculated as follows: drift gallons = tower flowrate gallons x % drift minute minute 100 Emissions from Tower in lbs/hour is calculated as follows: lbs = dissolved solids lbs x drift gallons x 60 minutes hour gallon minute hour Particulate Emissions from Tower in tons/year is calculated as follows: tons = lb x 8760 hours x tons x capacity factor year hour year 2000 lb PM10 and PM2.5 Emissions are Calculated as follows: PM10 Emissions = PM Emissions x % PM10 100 PM2.5 Emissions = PM Emissions x % PM2.5 100
% Mass Smaller = 100 - % Mass Larger Equation 7 from "Calculating Realistic PM10 Emissions from Cooling Towers", Joel Reisman and Gordon Frisbie, Environmental Progress, Volume 21, Issue 2, pages 127-130, July 2002: Diameter of Solid Particle μm = Diameter of Droplet μm x [Total Dissolved Solids ppmw x (Density of Water/Density of TDS)]1/3 Density of Water = 1.0 g . cm3 Density of TDS = Density of Sodium Chloride = 2.2 g . cm3 Diameter of Solid Particle μm = Diameter of Droplet μm x [Total Dissolved Solids parts x (1.0 g/cm3/2.2 g/cm3)]1/3 1,000,000 parts To Determine % Smaller than 10μm and less than 2.5μm, first calculate the droplet size that corresponds to the particle size: Diameter of Droplet μm = Diameter of Solid Particle μm . [Total Dissolved Solids parts x (1.0 g/cm3/2.2g/cm3)]^(1/3) 1,000,000 parts Then graph the cooling tower data to obtain the relationship between droplet size and % mass larger: This results in an exponential curve with the form % Mass Larger = 86.684e-(0.012x droplet diameter μm) Then calculate % Mass Smaller = 100 - % Mass Larger

## Cooling Tower HAPs
BOWIE POWER STATION COOLING TOWER HAP EMISSIONS
Cooling Tower Capacity Factor | 100%
CHLOROFORM
Cooling Towers
Corrected Emission Factor for Chloroform (kg/109 liters cooling water flow) From EPA document "Locating and Estimating Air Emissions from Sources of Chloroform, page 58 | 2.3 | kg/109 liters
Cooling water flow (gallons per minute) | 127860 | gallons/minute
Chloroform emissions from tower (lb/hour) | 0.14724 | lb/hour
Annual cooling tower chloroform emissions (tons/year) | 0.6449 | tons/year
BLOWDOWN EMISSIONS
Drift | 0.6393 | gallons/minute
| Blowdown Concentrationsa |  | Emissions
| ppb | lb/gallon | lb/hour | tons/year
Antimony | 36 | 3.004e-07 | 1.1523e-05 | 5.047e-05
Arsenic | 54 | 4.5061e-07 | 1.7284e-05 | 7.5705e-05
Beryllium | 9 | 7.5101e-08 | 2.8807e-06 | 1.2618e-05
Cadmium | 36 | 3.004e-07 | 1.1523e-05 | 5.047e-05
Chromium | 90 | 7.5101e-07 | 2.8807e-05 | 0.00012618
Lead | 36 | 3.004e-07 | 1.1523e-05 | 5.047e-05
Mercury | 4 | 3.3378e-08 | 1.2803e-06 | 5.6078e-06
Nickel | 90 | 7.5101e-07 | 2.8807e-05 | 0.00012618
Selenium | 36 | 3.004e-07 | 1.1523e-05 | 5.047e-05
aProvided in "Water Balance Flow Values", Kiewit Power Engineers
Cooling tower flow is from spreadsheet titled "Cooling Tower PM/PM10/PM2.5 Emissions" Chloroform lb = kg x 3.785 liters x 1000 g x lb x gallons x 60 minutes hour 109 liters gallon kg 453.59 grams minute hour tons = lb x 8760 hours x tons x capacity factor year hour year 2000 lb Drift value comes from spreadsheet titled "Cooling Tower PM/PM10/PM2.5 Emissions" For water, ppb = μg . liter lb = μg x 3.785 liters x grams x lb . gallon liter gallons 106 μg 453.59 grams lbs = solids lbs x drift gallons x 60 minutes hour gallon minute hour Emissions Per Tower in tons/year is calculated as follows: tons = lb x 8760 hours x tons year hour year 2000 lb

## Evaporation Pond Emissions
BOWIE POWER STATION EVAPORATION POND CHLOROFORM EMISSIONS
Chloroform Emissions
Corrected Emission Factor for Chloroform (kg/109 liters cooling water flow) From EPA document "Locating and Estimating Air Emissions from Sources of Chloroform, page 58 | 0.75
Flow to Cooling Ponds from all Cooling Towers combined (gallons per minute) | 131
Chloroform emissions from tower (lb/hour) | 4.919e-05
Annual chloroform emissions (tons/year) for 8760 hours/year | 0.00021545
lb = kg x 3.785 liters x 1000 g x lb x gallons x 60 minutes hour 109 liters gallon kg 453.59 grams minute hour tons = lb x 8760 hours x tons year hour year 2000 lb

## GHG Emissions
BOWIE POWER STATION ANNUAL GREENHOUSE GAS EMISSIONS
Number of Turbines and Duct Burners | 2
Number of Auxiliary Boilers | 1
Number of Emergency Fire Pumps | 1
Number of Circuit Breakers | 5
SF6 Contents (lbs)
Circuit Breaker - Each | 360
Turbine Heat Input - 59oF Ambient
Operating Scenario | Heat Input, mmBtu/hour HHV
100% Load | 1615.87
Minimum Compliance Load | 1020.8
Duct Burner Heat Input | 420 | mmBtu/hour HHV
Emission Unit | Heat Input Rate (mmBtu/hour) | Hours of Operation (hours/year) | Heat Input Rate (mmBtu/year) | Emission Factor |  |  |  | Emissions Each Piece of Equipment (tons/year)
|  |  |  | CO2a (kg/mmBtu) | CH4b (kg/mmBtu) | N2Ob (kg/mmBtu) | SF6 (% Leak Rate)c | CO2 | CH4 | N2O | SF6
Turbines - Startup | 1020.8 | 325 | 331760 | 53.02 | 0.001 | 0.0001 |  | 19392.8815 | 0.36577 | 0.036577
Turbines and Duct Burners - Duct Firing | 2035.87 | 4224 | 8599514.88 |  |  |  |  | 502680.7725 | 9.481 | 0.9481
Turbines - No Power Augmentation, No Duct Firing | 1615.87 | 3681.75 | 5949229.3725 |  |  |  |  | 347759.5258 | 6.559 | 0.6559
Turbines - Shutdown | 1020.8 | 91.25 | 93148 |  |  |  |  | 5444.9244 | 0.1027 | 0.01027
Turbines and Duct Burners - Oxidation Catalyst Conversion of CO | [7 empty] | 264.1479
Turbines and Duct Burners - Total | [7 empty] | 875542.2522 | 16.5085 | 1.6508
Auxiliary Boiler | 50 | 450 | 22500 | 53.02 | 0.001 | 0.0001 |  | 1315.2274 | 0.024806 | 0.0024806
Emergency Fire Pump | 1.8358 | 100 | 183.58 | 73.96 | 0.003 | 0.0006 |  | 14.9693 | 0.00060719 | 0.00012144
Circuit Breakers | [6 empty] | 0.1% |  |  |  | 0.00018
aFrom 40 Code of Federal Regulations 98, Table C-1, "Default CO2 Emission Factors and High Heat Values for Various Types of Fuel".
bFrom 40 Code of Federal Regulations 98, Table C-2, "Default CH4 and N2O Emission Factors for Various Types of Fuel".
cFrom Electric Power Substation Engineering, 2nd Edition, 2007, Edited by John D. McDonald. "Field checks of GIS [gas-insulated substations] in service after many years of service indicate that a leak rate objective lower than 0.1% per year is obtainable".
Emission Unit | CO2e Emissions per Piece of Equipment (tons/year) | CO2e Emissions Total (tons/year)
Turbines and Duct Burner | 876400.6917 | 1752801.3834
Auxiliary Boiler | 1316.5173 | 1316.5173
Emergency Fire Pump | 15.0197 | 15.0197
Circuit Breakers | 4.302 | 21.51
TOTAL | 877736.5307 | 1754154.4304
Oxidation Catalyst CO2 Emissions
| Uncontrolled CO Emissions (tons/year) | Controlled CO Emissions (tons/year) | CO Converted by Oxidation Catalyst (tons/year) | CO2 Emissions from Oxidation Catalyst Conversion from CO (tons/year)
Turbine and Duct Burner - Each (tons/year) | 248.6361 | 80.542 | 168.0941 | 264.1479
|  | CO2 | CH4 | N2O | SF6
Global Warming Potentiald |  | 1 | 21 | 310 | 23900
dFrom 40 CFR 98, Table A-1 "Global Warming Potentials"
Annual greenhouse gas (GHG) Emissions for the Combustion Turbines and Duct Burners are calculated in the same manner as emissions from the criteria pollutants - at an annual average ambient temperature of 59oF. For turbine startup and shutdown, a heat input equivalent to 50% load has been assumed. mmBtu = mmBtu x hours year hour year Combustion Emissions tons = Fuel Use mmBtu x kg x 2.205 lb x tons year year mmBtu kg 2000 lb Turbine and Duct Burner CO Controlled and Uncontrolled Emissions from spreadsheet "Turbine and Duct Burner Annual Emissions" CO Converted by Oxidation Catalyst tons = Uncontrolled CO Emissions tons - Controlled CO Emissions tons year year year Oxidation Catalyst CO2 Emissions tons = CO Converted by Oxidation Catalyst tons x 44 tons/ton moles of CO2 year year 28 tons/ton moles of CO Circuit Breaker SF6 Emissions tons = SF6 Content lb x % leak rate x tons . year year 2000 lb CO2e Emissions tons = (CO2 Emissions tons x CO2 Global Warming Potential) + (CH4 Emissions tons x CH4 Global Warming Potential) + (N2O Emissions tons x N2O Global Warming Potential) year year year year + (SF6 Emissions tons x SF6 Global Warming Potential) year Emissions Total tons = Emissions Each Piece of Equipment tons x # of Pieces of Equipment year year

## Modeling Data Summary
BOWIE POWER STATION MODELING DATA SUMMARY
Base Elevation |  | 1139 | meters
Pollutant | Averaging Periods | Modeling Scenario(s) | Emission Unit | Emission Rate (lb/hour) | Emission Rate (g/sec) | Stack Height (m) | Stack Exit Temperature (K) | Exit Velocity (m/sec) | Stack Diameter (m) | Operating Scenario for Emissions | Stack Parameter Scenario
NOx | 1-hour | NAAQS Vegetation and Soils Impacts | Turbines and Duct Burners | 101.32 | 12.766 | 54.8613 | 354.7611 | 17.0375 | 5.4861 | Hot Start - 10oF ambient used for months with average minimum temperature below freezing (December, January) | Startup Stack Parameters - 10oF ambient used for months with average minimum temperature below freezing (December, January)
|  |  |  | 87.08 | 10.9718 |  | 356.0389 | 15.9403 |  | Hot Start - 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Startup Stack Parameters - 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 92.82 | 11.6951 |  | 359.0389 | 15.1173 |  | Hot Start - 102oF ambient used for months with average maximum high over 90oF (June, July, August, September) | Startup Stack Parameters - 102oF ambient used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.55 | 0.069298 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Normal Operation
| 24-hour (Scenario 1) (Operating Scenario for Emissions and Stack Parameter Scenario match SO2 and PM2.5 scenario 1) | Secondary PM2.5 Impacts | Turbines and Duct Burners | 15.6 | 1.9656 | 54.8613 | 352.7056 | 21.335 | 5.4861 | Normal Operation - 10oF ambient, 100% load with duct firing used for months with average minimum temperature below freezing (December, January) | Normal Operation - 10oF ambient, 100% load with duct firing used for months with average minimum temperature below freezing (December, January)
|  |  |  | 14.7 | 1.8522 |  | 352.8722 | 19.811 |  | Normal Operation - 59oF ambient, 100% load with duct firing used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - 59oF ambient, 100% load with duct firing used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 14 | 1.764 |  | 353.7611 | 18.8967 |  | Normal Operation - 102oF ambient, 100% load with duct firing used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - 102oF ambient, 100% load with duct firing used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.275 | 0.034649 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Operation for 12 hours
|  |  | Emergency Fire Pump | 0.21018 | 0.026481 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Operation for 4 hours
| 24-hour (Scenario 2) (Operating Scenario for Emissions and Stack Parameter Scenario match SO2 and PM2.5 scenario 2) | Secondary PM2.5 Impacts | Turbines and Duct Burners | 9.1 | 1.1466 | 54.8613 | 356.0944 | 15.2393 | 5.4861 | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January) | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January)
|  |  |  | 7.4 | 0.93238 |  | 355.3167 | 13.1058 |  | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 7.4 | 0.93238 |  | 358.2056 | 13.7153 |  | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.275 | 0.034649 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Operation for 12 hours
|  |  | Emergency Fire Pump | 0.21018 | 0.026481 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Operation for 4 hours
NOx (continued) | Annual | NAAQS/AAAQS, Class I & II Increments, NOx Deposition, Vegetation and Soils Impacts | Turbines and Duct Burners | 15.8601 | 1.9983 | 54.8613 | 355.2348 | 18.1031 | 5.4861 | Annual average | Weighted average stack parameters 59oF ambient
|  |  | Auxiliary Boiler | 0.028253 | 0.0035599 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Annual average
|  |  | Emergency Fire Pump | 0.014396 | 0.0018138 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Annual average
CO | 1-hour and 8-hour | NAAQS/AAAQS, Vegetation and Soils Impacts | Turbines and Duct Burners | 262.28 | 33.0466 | 54.8613 | 355.3167 | 13.1058 | 5.4861 | Conservatively use Hot Start 10oF | Worst-case Stack Parameters - 59oF ambient, minimum compliance load
|  |  | Auxiliary Boiler | 1.85 | 0.23309 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Conservatively assume Normal Operation for all 8 hours
|  |  | Emergency Fire Pump | 0.81223 | 0.10234 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Conservatively assume Normal Operation for all 8 hours
SO2 | 1-hour and 3-hour (Scenario 1) | NAAQS/AAAQS | Turbines and Duct Burners | 4.1 | 0.51659 | 54.8613 | 352.7056 | 21.335 | 5.4861 | Normal Operation - 100% load with duct firing, 10oF ambient used for months with average minimum temperature below freezing (December, January) | Normal Operation - 100% load with duct firing, 10oF ambient used for months with average minimum temperature below freezing (December, January)
|  |  |  | 3.8 | 0.47879 |  | 352.8722 | 19.811 |  | Normal Operation - 100% load with duct firing, 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - 100% load with duct firing, 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 3.6 | 0.45359 |  | 353.7611 | 18.8967 |  | Normal Operation - 100% load with duct firing, 102oF ambient used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - 100% load with duct firing, 102oF ambient used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.10874 | 0.013701 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Normal Operation
|  |  | Emergency Fire Pump - 3-hour only | 0.0031551 | 0.00039753 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Normal Operation
| 1-hour and 3-hour (Scenario 2) | NAAQS/AAAQS | Turbines and Duct Burners | 3.6 | 0.45359 | 54.8613 | 354.7611 | 17.0375 | 5.4861 | Startup - 10oF ambient used for months with average minimum temperature below freezing (December, January) | Startup Stack Parameters - 10oF, used for months with average minimum temperature below freezing (December, January)
|  |  |  | 3.4 | 0.42839 |  | 356.0389 | 15.9403 |  | Startup - 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Startup Stack Parameters - 59oF used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 3.2 | 0.40319 |  | 359.0389 | 15.1173 |  | Startup - 102oF ambient used for months with average maximum high over 90oF (June, July, August, September) | Startup Stack Parameters - 102oF used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.10874 | 0.013701 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Normal Operation
|  |  | Emergency Fire Pump - 3-hour only | 0.0031551 | 0.00039753 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Normal Operation
SO2 (continued) | 1-hour and 3-hour (Scenario 3) | NAAQS/AAAQS | Turbines and Duct Burners | 2.6 | 0.32759 | 54.8613 | 356.0944 | 15.2393 | 5.4861 | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January) | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January)
|  |  |  | 2.1 | 0.26459 |  | 355.3167 | 13.1058 |  | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 2.1 | 0.26459 |  | 358.2056 | 13.7153 |  | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.10874 | 0.013701 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Normal Operation
|  |  | Emergency Fire Pump - 3-hour only | 0.0031551 | 0.00039753 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Normal Operation
| 24-hour (Scenario 1) | NAAQS/AAAQS | Turbines and Duct Burners | 4.1 | 0.51659 | 54.8613 | 352.7056 | 21.335 | 5.4861 | Normal Operation - 10oF ambient, 100% load with duct firing used for months with average minimum temperature below freezing (December, January) | Normal Operation - 10oF ambient, 100% load with duct firing used for months with average minimum temperature below freezing (December, January)
|  |  |  | 3.8 | 0.47879 |  | 352.8722 | 19.811 |  | Normal Operation - 59oF ambient, 100% load with duct firing used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - 59oF ambient, 100% load with duct firing used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 3.6 | 0.45359 |  | 353.7611 | 18.8967 |  | Normal Operation - 102oF ambient, 100% load with duct firing used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - 102oF ambient, 100% load with duct firing used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.054369 | 0.0068503 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Operation for 12 hours
|  |  | Emergency Fire Pump | 0.00052585 | 6.6256e-05 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Operation for 4 hours
SO2 (continued) | 24-hour (Scenario 2) | NAAQS/AAAQS | Turbines and Duct Burners | 2.6 | 0.32759 | 54.8613 | 356.0944 | 15.2393 | 5.4861 | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January) | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January)
|  |  |  | 2.1 | 0.26459 |  | 355.3167 | 13.1058 |  | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 2.1 | 0.26459 |  | 358.2056 | 13.7153 |  | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.054369 | 0.0068503 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Operation for 12 hours
|  |  | Emergency Fire Pump | 0.00052585 | 6.6256e-05 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Operation for 4 hours
| Annual | NAAQS/AAAQS | Turbines and Duct Burners | 3.425 | 0.43154 | 54.8613 | 355.2348 | 18.1031 | 5.4861 | Annual Average | Weighted average stack parameters 59oF
|  |  | Auxiliary Boiler | 0.0055858 | 0.0007038 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Annual Average
|  |  | Emergency Fire Pump | 3.6017e-05 | 4.5381e-06 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Annual Average
PM10 | 24-hour (Scenario 1) | NAAQS/AAAQS, Class I & II Increments, Vegetation and Soils Impacts | Turbines and Duct Burners | 8.5 | 1.071 | 54.8613 | 352.7056 | 21.335 | 5.4861 | Normal Operation - 10oF ambient, 100% load with duct firing used for months with average minimum temperature below freezing (December, January) | Normal Operation - 10oF ambient, 100% load with duct firing used for months with average minimum temperature below freezing (December, January)
|  |  |  | 8.5 | 1.071 |  | 352.8722 | 19.811 |  | Normal Operation - 59oF ambient, 100% load with duct firing used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - 59oF ambient, 100% load with duct firing used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 8.5 | 1.071 |  | 353.7611 | 18.8967 |  | Normal Operation - 102oF ambient, 100% load with duct firing used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - 102oF ambient, 100% load with duct firing used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.175 | 0.02205 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Operation for 12 hours
|  |  | Emergency Fire Pump | 0.011273 | 0.0014204 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Operation for 4 hours
|  |  | Cooling Towera | 0.097041 | 0.012227 | 14 | 294.2611 | 8.594 | 10 | Operation for 24 hours
PM10 (continued) | 24-hour (Scenario 2) | NAAQS/AAAQS, Class I & II Increments, Vegetation and Soils Impacts | Turbines and Duct Burners | 6.5 | 0.81898 | 54.8613 | 356.0944 | 15.2393 | 5.4861 | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January) | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January)
|  |  |  | 6.5 | 0.81898 |  | 355.3167 | 13.1058 |  | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 6.5 | 0.81898 |  | 358.2056 | 13.7153 |  | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.175 | 0.02205 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Operation for 12 hours
|  |  | Emergency Fire Pump | 0.011273 | 0.0014204 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Operation for 4 hours
|  |  | Cooling Towera | 0.097041 | 0.012227 | 14 | 294.2611 | 8.594 | 10 | Operation for 24 hours
| Annual | NAAQS/AAAQS, Class I & II Increments, Vegetation and Soils Impacts | Turbines and Duct Burners | 7.1394 | 0.89954 | 54.8613 | 355.2348 | 18.1031 | 5.4861 | Annual average | Weighted average stack parameters 59oF
|  |  | Auxiliary Boiler | 0.017979 | 0.0022654 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Annual average
|  |  | Emergency Fire Pump | 0.00077213 | 9.7286e-05 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Annual average
|  |  | Cooling Towera | 0.097041 | 0.012227 | 14 | 294.2611 | 8.594 | 10 | Annual average
PM2.5 | 24-hour (Scenario 1) | NAAQS/AAAQS, Class I & II Increments, Vegetation and Soils Impacts | Turbines and Duct Burners | 8.5 | 1.071 | 54.8613 | 352.7056 | 21.335 | 5.4861 | Normal Operation - 10oF ambient, 100% load with duct firing used for months with average minimum temperature below freezing (December, January) | Normal Operation - 10oF ambient, 100% load with duct firing used for months with average minimum temperature below freezing (December, January)
|  |  |  | 8.5 | 1.071 |  | 352.8722 | 19.811 |  | Normal Operation - 59oF ambient, 100% load with duct firing used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - 59oF ambient, 100% load with duct firing used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 8.5 | 1.071 |  | 353.7611 | 18.8967 |  | Normal Operation - 102oF ambient, 100% load with duct firing used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - 102oF ambient, 100% load with duct firing used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.175 | 0.02205 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Assume Normal Operation for 12 hours
|  |  | Emergency Fire Pump | 0.011273 | 0.0014204 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | 4 hours of operation
|  |  | Cooling Towera | 0.046246 | 0.0058269 | 14 | 294.2611 | 8.594 | 10 | Normal Operation
PM2.5 (continued) | 24-hour (Scenario 2) | NAAQS/AAAQS, Class I & II Increments, Vegetation and Soils Impacts | Turbines and Duct Burners | 6.5 | 0.81898 | 54.8613 | 356.0944 | 15.2393 | 5.4861 | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January) | Normal Operation - Minimum Compliance Load 10oF ambient used for months with average minimum temperature below freezing (December, January)
|  |  |  | 6.5 | 0.81898 |  | 355.3167 | 13.1058 |  | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November) | Normal Operation - Minimum Compliance Load 59oF ambient used for months where 10oF or 102oF not used (February, March, April, May, October, November)
|  |  |  | 6.5 | 0.81898 |  | 358.2056 | 13.7153 |  | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September) | Normal Operation - Minimum Compliance Load 102oF ambient used for months with average maximum high over 90oF (June, July, August, September)
|  |  | Auxiliary Boiler | 0.175 | 0.02205 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Assume Normal Operation for 12 hours
|  |  | Emergency Fire Pump | 0.011273 | 0.0014204 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | 4 hours of operation
|  |  | Cooling Towera | 0.046246 | 0.0058269 | 14 | 294.2611 | 8.594 | 10 | Normal Operation
| Annual | NAAQS/AAAQS, Class I & II Increments, Vegetation and Soils Impacts | Turbines and Duct Burners | 7.1394 | 0.89954 | 54.8613 | 355.2348 | 18.1031 | 5.4861 | Annual average | Weighted average stack parameters at 59oF ambient
|  |  | Auxiliary Boiler | 0.017979 | 0.0022654 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Annual average
|  |  | Emergency Fire Pump | 0.00077213 | 9.7286e-05 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | Annual average
|  |  | Cooling Towera | 0.046246 | 0.0058269 | 14 | 294.2611 | 8.594 | 10 | Annual average
NOx | 24-hour | Visibility Impacts | Turbines and Duct Burners | 22.0025 | 2.7723 | 54.8613 | 355.3618 | 13.2829 | 5.4861 | Each turbine - 3 hot starts, 2 shutdowns, remaining hours normal operation maximum emission rate of 100% load with duct firing, all 10oF ambient | Weighted average stack parameters at minimum compliance load 59oF ambient
|  |  | Auxiliary Boiler | 0.275 | 0.034649 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Assume Normal Operation for 12 hours
|  |  | Emergency Fire Pump | 0.21018 | 0.026481 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | 4 hours of operation
SO2 |  |  | Turbines and Duct Burners | 4.0583 | 0.51134 | 54.8613 | 355.3618 | 13.2829 | 5.4861 | Each turbine - 3 hot starts, 2 shutdowns, remaining hours normal operation maximum emission rate of 100% load with duct firing, all 10oF ambient | Weighted average stack parameters at minimum compliance load 59oF ambient
|  |  | Auxiliary Boiler | 0.054369 | 0.0068503 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Assume Normal Operation for 12 hours
|  |  | Emergency Fire Pump | 0.00052585 | 6.6256e-05 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | 4 hours of operation
PM10/PM2.5 |  |  | Turbines and Duct Burners | 8.3333 | 1.05 | 54.8613 | 355.3618 | 13.2829 | 5.4861 | Each turbine - 3 hot starts, 2 shutdowns, remaining hours normal operation maximum emission rate of 100% load with duct firing, emissions assumed to be the same at all temperatures | Weighted average stack parameters at minimum compliance load 59oF ambient
|  |  | Auxiliary Boiler | 0.175 | 0.02205 | 13.7 | 422.0389 | 15.2393 | 0.76196 | Assume Normal Operation for 12 hours
|  |  | Emergency Fire Pump | 0.011273 | 0.0014204 | 10.6675 | 809.2611 | 65.2321 | 0.12699 | 4 hours of operation
|  |  | Cooling Towera | 0.097041 | 0.012227 | 14 | 294.2611 | 8.594 | 10 | Normal Operation
aThere are 9 cooling tower cells. Data shown are for each cell individually.
Maximum Turbine Short-term Emission Rates: NOx - Maximum emission rate occurs during hot starts. Hot start emission rates are much higher than normal operation emission rates. CO - Maximum emission rate occurs during hot starts PM10/PM2.5 - Maximum emission rate occurs at 100% turbine load plus duct firing,. Startup emission are assumed to equal normal operation emissions without duct firing, maximum emission rate occurs at 100% turbine load. SO2 - Maximum emission rate occurs at 100% turbine load plus duct firing,. Startup emission are assumed to equal normal operation emissions without duct firing, maximum emission rate occurs at 100% turbine load Worst-Case Turbine Stack Parameters from Screening Modeling occur at: 59oF ambient temperature, minimum compliance load case Short-term Emission Rates for turbines are from spreadsheets titled "Turbine and Duct Burner Hourly Emissions" and "Turbine Startup Emissions" Short-term Emission rates for non-turbine emission units are from "One Hour Emission Criteria Pollutant Emission Summary" 24-hour Average Emission Rate for auxiliary boiler and fire pump SO2 and PM10/PM2.5 lb = lb x hours of operation hour hour 24 hours 24-hour Emission Rates for visibility impacts are from "24-Hour Modeling Scenario Emissions" Annual Average Emission Rates are from "Annual Project Criteria Pollutant Emissions" Annual Averages Emissions lb = tons x year x 2000 lb hour year 8760 hours ton Cooling Tower Emissions are divided by 9 to apportion the emissions among the 9 cooling tower cells grams = lb x 453.59 grams x hour . second hour lb 3600 seconds Short-term stack parameters are from the spreadsheet titled "Turbine Stack Parameters" Annual stack parameters are from the spreadsheet titled "Turbine and Duct Burner Annual Weighted Average Stack Parameters"

## Modeling - Screening Parameters
BOWIE POWER STATION TURBINE AND DUCT BURNER SCREENING STACK PARAMETERS
Base Elevation |  | 1139 | meters
Load | Ambient Temperature (oF) | Duct Burners | Stack Height (m) | Stack Exit Temperature (K) | Exit Velocity (m/sec) | Stack Diameter (m)
100% | 10 | Yes | 54.8613 | 352.7056 | 21.335 | 5.4861
100% | 59 | Yes | 54.8613 | 352.8722 | 19.811 | 5.4861
100% | 102 | Yes | 54.8613 | 353.7611 | 18.8967 | 5.4861
100% | 10 | No | 54.8613 | 361.8167 | 21.6397 | 5.4861
100% | 59 | No | 54.8613 | 361.7056 | 20.1158 | 5.4861
100% | 102 | No | 54.8613 | 362.7611 | 19.2015 | 5.4861
80% | 10 | No | 54.8613 | 358.2611 | 17.6775 | 5.4861
80% | 59 | No | 54.8613 | 357.8722 | 16.4584 | 5.4861
80% | 102 | No | 54.8613 | 358.4833 | 14.9345 | 5.4861
Minimum Compliance Load | 10 | No | 54.8613 | 356.0944 | 15.2393 | 5.4861
Minimum Compliance Load | 59 | No | 54.8613 | 355.3167 | 13.1058 | 5.4861
Minimum Compliance Load | 102 | No | 54.8613 | 358.2056 | 13.7153 | 5.4861
Startup | 10 | No | 54.8613 | 354.7611 | 17.0375 | 5.4861
Startup | 59 | No | 54.8613 | 356.0389 | 15.9403 | 5.4861
Startup | 102 | No | 54.8613 | 359.0389 | 15.1173 | 5.4861
Stack Parameters are from spreadsheet titled "Turbine+Duct Burner Info"

## Turbine+Duct Burner stack info
BOWIE POWER STATION TURBINE STACK PARAMETERS
| feet | meters
Base Elevation |  | 1139
Stack Height | 180 | 54.8613
Stack Diameter | 18 | 5.4861
Stack Temperature |  | oF
Ambient Temperature
Configuration | Load | 10oF | 59 oF | 102 oF
Startup | Startup | 178.9 | 181.2 | 186.6
Turbine + Duct Firing | 100% | 175.2 | 175.5 | 177.1
Turbine | 100% | 191.6 | 191.4 | 193.3
Turbine | 80% | 185.2 | 184.5 | 185.6
Turbine | Minimum Compliance Load | 181.3 | 179.9 | 185.1
Stack Temperature |  | K
Ambient Temperature
Configuration | Load | 10oF | 59 oF | 102 oF
Startup | Startup | 354.7611 | 356.0389 | 359.0389
Turbine + Duct Firing | 100% | 352.7056 | 352.8722 | 353.7611
Turbine | 100% | 361.8167 | 361.7056 | 362.7611
Turbine | 80% | 358.2611 | 357.8722 | 358.4833
Turbine | Minimum Compliance Load | 356.0944 | 355.3167 | 358.2056
Exit Velocity |  | ft/second
Ambient Temperature
Configuration | Load | 10oF | 59 oF | 102 oF
Startup | Startup | 55.9 | 52.3 | 49.6
Turbine + Duct Firing | 100% | 70 | 65 | 62
Turbine | 100% | 71 | 66 | 63
Turbine | 80% | 58 | 54 | 49
Turbine | Minimum Compliance Load | 50 | 43 | 45
Exit Velocity |  | meters/sec
Ambient Temperature
Configuration | Load | 10oF | 59 oF | 102 oF
Startup | Startup | 17.0375 | 15.9403 | 15.1173
Turbine + Duct Firing | 100% | 21.335 | 19.811 | 18.8967
Turbine | 100% | 21.6397 | 20.1158 | 19.2015
Turbine | 80% | 17.6775 | 16.4584 | 14.9345
Turbine | Minimum Compliance Load | 15.2393 | 13.1058 | 13.7153
meters = feet x meters 3.281 feet K =[ 5 x (oF - 32)] + 273.15 9 meters = feet x meters . second second 3.281 feet

## Turbine Stack Data Weighted Ave
BOWIE POWER STATION TURBINE AND DUCT BURNER WEIGHTED AVERAGE STACK PARAMETERS
Annual
Ambient Temperature |  | 59oF
Configuration | Load | Stack Temperature (K) | Exit Velocity (meters/sec) | Hours per Year
Cold Startup | Startup | 356.0389 | 15.9403 | 325
Turbine + Duct Firing | 100% | 352.8722 | 19.811 | 4224
Turbine | 80% | 357.8722 | 16.4584 | 3681.75 | Assumed for all turbine-only hours
Turbine | Shutdown | 355.3167 | 13.1058 | 91.25 | Use for shutdown hours
Weighted Average |  | 355.2348 | 18.1031
|  | oF | feet/sec |  | For "Emission Sources" Forms
|  | 179.7526 | 59.3963
Three Hot Starts, Two Shutdowns + Turbine Operation at Minimum Compliance Load
| 10oF |  | 59oF |  | 102oF |  | Duration (hours)
| Stack Temperature (K) | Exit Velocity (meters/sec) | Stack Temperature (K) | Exit Velocity (meters/sec) | Stack Temperature (K) | Exit Velocity (meters/sec)
Three Hot Starts | 354.7611 | 17.0375 | 356.0389 | 15.9403 | 359.0389 | 15.1173 | 1.5 | Use Cold Start Data
Two Shutdowns | 356.0944 | 15.2393 | 355.3167 | 13.1058 | 358.2056 | 13.7153 | 0.5 | Use Minimum Compliance Load Data
Normal Operation without Duct Firing - Minimum Compliance Load | 356.0944 | 15.2393 | 355.3167 | 13.1058 | 358.2056 | 13.7153 | 22
Weighted Average | 356.0111 | 15.3516 | 355.3618 | 13.2829 | 358.2576 | 13.803
Delete after confirming modeling scenarios
Stack data is from "Turbine Stack Parameters" spreadsheet Hours per year are from "Turbine and Duct Burner Annual" spreadsheet Startup and shutdown durations are from "Turbine Startup Emissions" spreadsheet Weighted Average Temperature = Σ(Configuration Temperature x Configuration Hours) Total Hours Weighted Average Exit Velocity = Σ(Configuration Exit Velocity x Configuration Hours) Total Hours oF = ((K - 273.15) x 9) + 32 5 feet = meters x 3.281 feet second second meters

## 24-hour Crit Emissions Summary
BOWIE STATION 24-HOUR VISIBILITY MODELING SCENARIO EMISSIONS
Total Number of Turbines = | 2
Number of Turbines Undergoing Hot Start during 24 hour period = | 2
Hours in Hot Startup For Each Turbine in startup mode during 24 hour period = | 1.5 | 3 hot starts each turbine
Number of Turbines Undergoing Warm Start during 24 hour period = | 0
Hours in Warm Startup For Each Turbine in startup mode during 24 hour period = | 0
Number of Turbines Undergoing Cold Start during 24 hour period = | 0
Hours in Cold Startup For Each Turbine in startup mode during 24 hour period = | 0
Number of Turbines Undergoing Shutdown during 24 hours period = | 2
Hours in Shutdown for Each Turbine during 24 hour period = | 0.5 | 2 shutdowns each turbine
Hours of Operation Each Auxiliary Boiler in 24 hour period = | 12
Hours of Operation of Emergency Fire Pump in 24 hour period = | 4
Hours of Operation of Cooling Towers in 24 hour period = | 24
| NOx | VOCs | SO2a | PM10a
Turbine Emissions (lb)
Total Emissions from Hot Starts | 303.96 | 52.68 | 10.8 | 19.5 | lb
Total Emissions from Warm Starts | 0 | 0 | 0 | 0 | lb
Total Emissions from Cold Starts | 0 | 0 | 0 | 0 | lb
Total Emissions for Shutdown | 65.76 | 25.72 | 3.6 | 6.5 | lb
Emissions from normal operationb | 686.4 | 180.4 | 180.4 | 374 | lb
Total Turbine and Duct Burner Emissions during 24-hour period | 1056.12 | 258.8 | 194.8 | 400 | lb
Average Emission Rate Each Turbine and Duct Burner Pair (lb/hour) | 22.0025 | 5.3917 | 4.0583 | 8.3333 | lb/hour
aStartup and shutdown emissions from SO2 and PM10 are assumed to be equivalent to the maximum turbine only (no duct firing) normal operation emissions
bIncludes duct burner emissions.
Pounds/Hour Per Hour Per Piece of Equipment | Emissions (lb/hour)
| NOx | VOCs | SO2 | PM10
Per Turbine and Duct Burner (average 24-hour emission rate, startup for designated number of hours, normal operation for remaining hours) | 22.0025 | 5.3917 | 4.0583 | 8.3333
Auxiliary Boiler | 0.275 | 0.1 | 0.054369 | 0.175
Emergency Fire Pump | 0.21018 | 0.011751 | 0.00052585 | 0.011273
Cooling Tower | -- | 0.14724 | -- | 0.87337
Tons/Day
Equipment
Turbines and Duct Burners | 2
Auxiliary Boilers | 1
Emergency Fire Pumps | 1
Cooling Towers | 1
Tons Per Day Per Piece of Equipment | Emissions (tons/day)
| NOx | VOCs | SO2 | PM10
Per Turbine and Duct Burner (startup for designated number of hours, normal operation for remaining hours) | 0.26403 | 0.0647 | 0.0487 | 0.1
Per Auxiliary Boiler | 0.0033 | 0.0012 | 0.00065243 | 0.0021
Per Emergency Fire Pump | 0.0025221 | 0.00014101 | 6.3102e-06 | 0.00013528
Per Cooling Tower | -- | 0.0017668 | -- | 0.01048
Tons Per Day For All Pieces of Equipment | Emissions (tons/day)
| NOx | VOCs | SO2 | PM10
All Turbine and Duct Burners (startup for designated number of hours, normal operation for remaining hours) | 0.52806 | 0.1294 | 0.0974 | 0.2
Auxiliary Boiler | 0.0033 | 0.0012 | 0.00065243 | 0.0021
Emergency Fire Pump | 0.0025221 | 0.00014101 | 6.3102e-06 | 0.00013528
Cooling Tower | -- | 0.0017668 | -- | 0.01048
24-Hour NOx Emission Scenario For the 24-hour modeling scenario assume that a designated number of turbines go through hot, warm, or cold startup during the 24-hour period. For the remaining hours, assume the turbine emits at the maximum rate.
24 - Hour NOx Emission Rate Calculation for Turbines Emissions Start (lb) = # of turbines in start x hours in startup x lb . turbine hour Emissions Shutdown (lb) = # of turbines in shutdown x hours in shutdown x shutdown x lb . turbine hour shutdown Emissions from Normal Operation for Turbines (lb) = # of turbines x (24 hours - hours in startup and shutdown) x lb (controlled) normal operation turbine hour Total Emissions 24-hour Period = Emissions from Hot Starts + Emissions from Warm Starts + Emissions from Cold Starts + Emissions from Shutdowns + Emissions from Normal Operation for Turbines Average Emission Rate Each Turbine lb = lb all turbines for 24 hour period x 1 x 1 . hour 24 hours # of turbines Conversion from lb/hour to tons/day tons = lb x hours x tons day hour day 2000 lb Calculation of Emissions in tons/day from all equipment tons = tons x # of pieces of Equipment day day