## Baseline Actual Emissions (hidden)
Table D-1
Unit 1 and Unit 2 - Baseline Actual Emissions
Salt River Project - Coronado Generating Station
| 2005 Pre-Construction |  | 2006 Pre-Construction |  | Notes
| Unit 1 | Unit 2 | Unit 1 | Unit 2
Unit Design Information
Maximum Boiler Heat Input (mmBtu/hr) | 4535 | 4390 | 4517 | 4419 | Maximum value from operating records
Boiler Heat Input (mmBtu/yr) | 34140468.9 | 30937528.7 | 35135615.9 | 28768460 | Fourth Quarter EDR Reports for 2005 and 2006
Operating Hours (hr/yr) | 8494 | 8603 | 8589 | 7883 | Fourth Quarter EDR Reports for 2005 and 2006
Coal Burned (tpy) | 1620484 | 1725470 | 1722491 | 1551360 | CGS December 2005 and 2006 Monthly Operating Reports
Coal Burned (lbs/hr) | 381559.6892 | 401132.1632 | 401092.3274 | 393596.3466 | [Coal Burned (tpy) x 2,000 lb/ton] / Operating Hours (hr/yr)
Oil Burned (bbl/yr) | 5490 | 4147 | 6742 | 5047 | CGS December 2005 and 2006 Monthly Operating Reports
Oil Burned (gal/yr) | 230580 | 174174 | 283164 | 211974 | Oil Burned (bbl/yr) x 42 gal/bbl
Coal Heating Value (Btu/lb) | 9719 | 9197 | 9447 | 9340 | CGS December 2005 and 2006 Monthly Operating Reports
Oil Heating Value (Btu/gal) | 140179 | 140179 | 139990 | 139990 | CGS December 2005 and 2006 Monthly Operating Reports
Coal Data
Sulfur Content (%) | 0.54 | 0.54 | 0.54 | 0.54 | Baseline value is assumed equivalent to post-construction engineering assumption based on SRP coal analyses
Oil Data
Oil Sulfur Content (%) | 0.1 | 0.1 | 0.1 | 0.1 | Fuel Oil Analyses (no sulfur content detected, so detection limit assumed)
Coal Emissions
NOx (tpy) | 7306.0603 | 6713.4437 | 6500.0889 | 6084.5293 | [NOx (lb/mmBtu) x Boiler Heat Input (mmBtu/yr)]/ 2,000 lb/ton
NOx (lb/hr) | 1940.98 | 1905.26 | 1671.29 | 1869.237 | NOx (lb/mmBtu) x Maximum Boiler Heat Input (mmBtu/hr)
NOx (lb/mmBtu) annual average | 0.428 | 0.434 | 0.37 | 0.423 | Fourth Quarter EDR Reports for 2005 and 2006
SO2 (tpy) | 5473.3 | 5003.1 | 7628.8 | 5886.7 | SO2 (lb/mmBtu) x Maximum Boiler Heat Input (mmBtu/hr)
SO2 (lb/hr) | 1454.0758 | 1419.8684 | 1961.502 | 1808.4616 | [SO2 (tpy) x 2,000 lb/ton] / Operating Hours (hr/yr)
SO2 (lb/mmBtu) Annual average | 0.32063 | 0.32343 | 0.43425 | 0.40925 | [SO2 (tpy) x 2,000 lb/ton] / Boiler Heat Input (mmBtu/yr)
Filterable PM (tpy) | 512.107 | 464.0629 | 527.0342 | 431.5269 | [Filterable PM (lb/mmBtu) x Boiler Heat Input (mmBtu/yr)]/ 2,000 lb/ton
Filterable PM (lb/hr) | 136.05 | 131.7 | 135.51 | 132.57 | Filterable PM (lb/mmBtu) x Maximum Boiler Heat Input (mmBtu/hr)
Filterable PM (lb/mmBtu) | 0.03 | 0.03 | 0.03 | 0.03 | Assumed equivalent to post-construction proposed emission limit (conservative since current permit limit is 0.10 lb/mmBtu)
Filterable PM10 (tpy) | 512.107 | 464.0629 | 527.0342 | 431.5269 | Assume equivalent to filterable PM emissions
Filterable PM10 (lb/hr) | 136.05 | 131.7 | 135.51 | 132.57 | Assume equivalent to filterable PM emissions
Filterable PM10 (lb/mmBtu) | 0.03 | 0.03 | 0.03 | 0.03 | Assume equivalent to filterable PM emissions
Condensable PM10 (tpy) | 160.0997 | 150.5407 | 170.8311 | 140.0114 | [Condensable PM10 (lb/mmBtu) x Boiler Heat Input (mmBtu/yr)]/ 2,000 lb/ton
Condensable PM10 (lb/hr) | 42.5332 | 42.7231 | 43.9238 | 43.0131 | Condensable PM10 (lb/mmBtu) x Maximum Boiler Heat Input (mmBtu/hr)
Condensable PM10 (lb/mmBtu) | 0.0093789 | 0.0097319 | 0.0097241 | 0.0097337 | H2SO4 (lb/mmBtu) + 0.005 lb/mmBtu (conservatively assumed remaining condensable would be equivalent to H2SO4 emissions at full capacity)
Total PM10 (tpy) | 672.2067 | 614.6037 | 697.8653 | 571.5383 | Filterable PM10 (tpy) + Condensable PM10 (tpy)
Total PM10 (lb/hr) | 178.5832 | 174.4231 | 179.4338 | 175.5831 | Filterable PM10 (lb/hr) + Condensable PM10 (lb/hr)
Total PM10 (lb/mmBtu) | 0.039379 | 0.039732 | 0.039724 | 0.039734 | Filterable PM10 (lb/mmBtu) + Condensable PM10 (lb/mmBtu)
HCl (tpy) | 42.6756 | 38.6719 | 43.9195 | 35.9606 | [HCl (lb/mmBtu) x Boiler Heat Input (mmBtu/yr)] / 2,000 lb/ton
HCl (lb/hr) | 11.3375 | 10.975 | 11.2925 | 11.0475 | HCl (lb/mmBtu) x Maximum Boiler Heat Input (mmBtu/hr)
HCl (lb/mmBtu) | 0.0025 | 0.0025 | 0.0025 | 0.0025 | Engineering assumption based on EPRI studies
HF (tpy) | 34.1405 | 30.9375 | 35.1356 | 28.7685 | [HF (lb/mmBtu) x Boiler Heat Input (mmBtu/yr)] / 2,000 lb/ton
HF (lb/hr) | 9.07 | 8.78 | 9.034 | 8.838 | HF (lb/mmBtu) x Maximum Boiler Heat Input (mmBtu/hr)
HF (lb/mmBtu) | 0.002 | 0.002 | 0.002 | 0.002 | Engineering assumption based on EPRI studies
H2SO4 (tpy) | 74.1583 | 79.2048 | 81.7606 | 67.5914 | Material Balance
H2SO4 (lb/hr) | 19.8582 | 20.7731 | 21.3388 | 20.9181 | Material Balance
H2SO4 (lb/mmBtu) | 0.0043789 | 0.0047319 | 0.0047241 | 0.0047337 | Material Balance
CO (tpy) | 405.121 | 431.3675 | 430.6227 | 387.84 | [CO (lb/ton) x Coal Burned (tpy)] / 2,000 lb/ton
CO (lb/hr) | 95.3899 | 100.283 | 100.2731 | 98.3991 | [CO (lb/ton) x Coal Burned (lb/hr)] / 2,000 lb/ton
CO (lb/ton) | 0.5 | 0.5 | 0.5 | 0.5 | EPA AP-42 Emission Factor, Table 1.1-3
VOC (tpy) | 48.6145 | 51.7641 | 51.6747 | 46.5408 | [VOC (lb/ton) x Coal Burned (tpy)] / 2,000 lb/ton
VOC (lb/hr) | 11.4468 | 12.034 | 12.0328 | 11.8079 | VOC (lb/ton) x [Coal Burned (lb/hr) / 2,000 lb/ton]
VOC (lb/ton) | 0.06 | 0.06 | 0.06 | 0.06 | EPA AP-42 Emission Factor, Table 1.1-19
Lead (tpy) | 8.6546 | 7.8427 | 8.9069 | 7.2928 | [Lead (lb/mmBtu) x Boiler Heat Input (mmBtu/yr)] / 2,000 lb/ton
Lead (lb/hr) | 2.2992 | 2.2257 | 2.2901 | 2.2404 | Lead (lb/mmBtu) x Maximum Boiler Heat Input (mmBtu/hr)
Lead (lb/mmBtu) | 0.000507 | 0.000507 | 0.000507 | 0.000507 | EPA AP-42 Emission Factor, Table 1.1-17
Mercury (tpy) | 0.14168 | 0.12839 | 0.14581 | 0.11939 | [Mercury (lb/mmBtu) x Boiler Heat Input (mmBtu/yr)] / 2,000 lb/ton
Mercury (lb/hr) | 0.037641 | 0.036437 | 0.037491 | 0.036678 | Mercury (lb/mmBtu) x Maximum Boiler Heat Input (mmBtu/hr)
Mercury (lb/mmBtu) | 8.3e-06 | 8.3e-06 | 8.3e-06 | 8.3e-06 | Assumes average coal Hg content is 8.7 lb/Tbtu - 15% oxidation by boilers, 45% oxidation by scrubbers, and 35% flue gas bypasses scrubbers
Oil Emissions
NOx (oil, tpy) | 2.767 | 2.0901 | 3.398 | 2.5437 | [NOx (oil, lb/1,000 gal) / 1,000)] x Oil Burned (gal/yr) x 1 ton / 2,000 lb
NOx (oil, lb/hr) | 0.65151 | 0.4859 | 0.79124 | 0.64536 | (NOx (oil, tpy) x 2,000 lb/ton) / Operating Hours (hr/yr)
NOx (oil, lb/1,000 gal) | 24 | 24 | 24 | 24 | EPA AP-42 Emission Factor, Table 1.3-1
CO (oil, tpy) | 0.57645 | 0.43544 | 0.70791 | 0.52994 | [CO (oil, lb/1,000 gal) / 1,000)] x Oil Burned (gal/yr) x 1 ton / 2,000 lb
CO (oil, lb/hr) | 0.13573 | 0.10123 | 0.16484 | 0.13445 | (CO (oil, tpy) x 2,000 lb/ton) / Operating Hours (hr/yr)
CO (oil, lb/1,000 gal) | 5 | 5 | 5 | 5 | EPA AP-42 Emission Factor, Table 1.3-1
VOC (oil, tpy) | 0.08762 | 0.066186 | 0.1076 | 0.08055 | [VOC (oil, lb/1,000 gal) / 1,000)] x Oil Burned (gal/yr) x 1 ton / 2,000 lb
VOC (oil, lb/hr) | 0.020631 | 0.015387 | 0.025056 | 0.020436 | (VOC (oil, tpy) x 2,000 lb/ton) / Operating Hours (hr/yr)
VOC (oil, lb/1,000 gal) | 0.76 | 0.76 | 0.76 | 0.76 | EPA AP-42 Emission Factor, Table 1.3-3 (NMTOC)
SO2 (oil, tpy) | 1.8101 | 1.3673 | 2.2228 | 1.664 | [SO2 (oil, lb/1,000 gal) / 1,000)] x Oil Burned (gal/yr) x 1 ton / 2,000 lb
SO2 (oil, lb/hr) | 0.4262 | 0.31786 | 0.5176 | 0.42217 | (SO2 (oil, tpy) x 2,000 lb/ton) / Operating Hours (hr/yr)
SO2 (oil, lb/1,000 gal) | 15.7 | 15.7 | 15.7 | 15.7 | EPA AP-42 Emission Factor, Table 1.3-1 (157 x Fuel Oil Sulfur Content)
PM (oil, tpy) | 0.38046 | 0.28739 | 0.46722 | 0.34976 | [PM (oil, lb/1,000 gal) / 1,000)] x Oil Burned (gal/yr) x 1 ton / 2,000 lb
PM (oil, lb/hr) | 0.089583 | 0.066811 | 0.1088 | 0.088737 | (PM (oil, tpy) x 2,000 lb/ton) / Operating Hours (hr/yr)
PM (oil, lb/1,000 gal) | 3.3 | 3.3 | 3.3 | 3.3 | EPA AP-42 Emission Factor, Tables 1.3-1 and 1.3-2
Capacity Factor
Capacity Factor (%) | 87.93 | 88.64 | 89.22 | 81.98 | CGS December 2005 and 2006 Monthly Operating Reports

## H2SO4 Emissions (hidden)
Table D-3
Unit 1 and Unit 2 - Sulfuric Acid Mist Emissions
Salt River Project - Coronado Generating Station
| 2005 Pre-Construction |  | 2006 Pre-Construction |  | Post-Construction |  | Notes
| Unit 1 | Unit 2 | Unit 1 | Unit 2 | Unit 1 | Unit 2
Unit Design Information
Maximum Boiler Heat Input (mmBtu/hr) | 4535 | 4390 | 4517 | 4419 | #REF! | #REF! | Pre-construction is maximum value from operating records; post-construction is maximum capacity
Boiler Heat Input (mmBtu/yr) | 34140468.9 | 30937528.7 | 35135615.9 | 28768460 | #REF! | #REF! | Pre-construction is Fourth Quarter EDR Reports for 2005 and 2006; post-construction is maximum capacity
Operating Hours (hr/yr) | 8494 | 8603 | 8589 | 7883 | #REF! | #REF! | Pre-construction is Fourth Quarter EDR Reports for 2005 and 2006; post-construction is maximum capacity
Coal Burned (tpy) | 1620484 | 1725470 | 1722491 | 1551360 | #REF! | #REF! | Pre-construction is CGS December 2005 and 2006 Monthly Operating Reports; post-construction is engineering assumption
Coal Heating Value (Btu/lb) | 9719 | 9197 | 9447 | 9340 | #REF! | #REF! | Pre-construction is CGS December 2005 and 2006 Monthly Operating Reports; post-construction is engineering assumption
Coal Data
Sulfur Content (%) | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | Pre-construction is assumed equivalent to post-construction engineering assumption based on SRP coal analyses
Capacity Factor
Capacity Factor (%) | 87.93 | 88.64 | 89.22 | 81.98 | 100 | 100 | Pre-construction is CGS December 2005 and 2006 Monthly Operating Reports; post-construction is maximum capacity
H2SO4 Calculation Assumptions
CB (%) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Conversion of SO2 to SO3 in the boiler - engineering assumption
MWSO3 | 80 | 80 | 80 | 80 | 80 | 80 | Molecular weight of SO3
MWSO2 | 64 | 64 | 64 | 64 | 64 | 64 | Molecular weight of SO2
MWS | 32 | 32 | 32 | 32 | 32 | 32 | Molecular weight of S
CF | 525 | 525 | 525 | 525 | 525 | 525 | Factor used to convert from lb/mmBtu to ppmvd at 3 percent oxygen
CHESP (ppm) | 1 | 1 | 1 | 1 | 1 | 1 | Reduction in SO3 emissions in the HESP - engineering assumption
CAPH (%) | 10 | 10 | 10 | 10 | 10 | 10 | Reduction in SO3 emissions in the air preheater - engineering assumption
CFGD (%) | 20 | 20 | 20 | 20 | 20 | 20 | Reduction in SO3 emissions in the FGD - engineering assumption
CC (%) | ----- | ----- | ----- | ----- | ----- | 0.5 | Catalyst oxidation of SO2 to SO3 - engineering assumption
MWH2SO4 | 98 | 98 | 98 | 98 | 98 | 98 | Molecular weight of H2SO4
FGS (%) | 64.9 | 67.2 | 50.3 | 57 | 100 | 100 | Percentage of flue gas processed in scrubber (2005 and 2006 data from operating records)
Total H2SO4 Emissions without SCR
SO2 Inlet (lb/mmBtu) | 1.1112 | 1.1743 | 1.1432 | 1.1563 | #REF! | #REF! | [(Sulfur Content (%) / 100) x (MWSO2 / MWS) x 1,000,000 Btu/mmBtu] / Coal Heating Value (Btu/lb)
SO3 Boiler Outlet (lb/hr) | 31.4963 | 32.2197 | 32.2745 | 31.936 | #REF! | #REF! | Maximum Boiler Heat Input (mmBtu/hr) x SO2 Inlet (lb/mmBtu) x (CB / 100) x (MWSO3 / MWSO2)
SO3 Boiler Outlet (ppm) | 2.917 | 3.0825 | 3.001 | 3.0353 | #REF! | #REF! | SO2 Inlet (lb/mmBtu) x (CB / 100) x CF
SO3 Air Preheater Inlet (lb/hr) | 20.6987 | 21.7674 | 21.5198 | 21.4146 | #REF! | #REF! | [SO3 Air Preheater Inlet (ppm) / SO3 Boiler Outlet (ppm)] x SO3 Boiler Outlet (lb/hr)
SO3 Air Preheater Inlet (ppm) | 1.917 | 2.0825 | 2.001 | 2.0353 | #REF! | #REF! | SO3 Boiler Outlet (ppm) - CHESP (ppm)
SO3 Air Preheater Outlet (lb/hr) | 18.6288 | 19.5906 | 19.3678 | 19.2731 | #REF! | #REF! | SO3 Air Preheater Inlet (lb/hr) x [1 - (CAPH / 100)]
SO3 Air Preheater Outlet (ppm) | 1.7253 | 1.8743 | 1.8009 | 1.8318 | #REF! | #REF! | SO3 Air Preheater Inlet (ppm) x [1 - (CAPH / 100)]
SO3 FGD Inlet (lb/hr) | 18.6288 | 19.5906 | 19.3678 | 19.2731 | #REF! | #REF! | SO3 Air Preheater Outlet (lb/hr)
SO3 FGD Inlet (ppm) | 1.7253 | 1.8743 | 1.8009 | 1.8318 | #REF! | #REF! | SO3 Air Preheater Outlet (ppm)
SO3 FGD Outlet (lb/hr) | 16.2108 | 16.9576 | 17.4194 | 17.076 | #REF! | #REF! | [(1-(FGS/100)) x SO3 FGD Inlet (lb/hr)] + [(FGS/100) x SO3 FGD Inlet (lb/hr) x [1 - (CFGD / 100)]]
SO3 FGD Outlet (ppm) | 1.5013 | 1.6224 | 1.6197 | 1.623 | #REF! | #REF! | [(1-(FGS/100)) x SO3 FGD Inlet (ppm)] + [(FGS/100) x SO3 FGD Inlet (ppm) x [1 - (CFGD / 100)]]
H2SO4 without SCR (tpy) | 74.1583 | 79.2048 | 81.7606 | 67.5914 | #REF! | #REF! | SO3 FGD Outlet (lb/hr) x (MWH2SO4 / MWSO3) x Operating Hours (hr/yr) x (Capacity Factor (%) / 100) x (1 ton / 2,000 lb)
H2SO4 without SCR (lb/hr) | 19.8582 | 20.7731 | 21.3388 | 20.9181 | #REF! | #REF! | [H2SO4 without SCR (tpy) x (2,000 lb / ton)] / Operating Hours (hr/yr)
H2SO4 without SCR (lb/mmBtu) | 0.0043789 | 0.0047319 | 0.0047241 | 0.0047337 | #REF! | #REF! | [SO2 FGD Outlet (lb/hr) x (MWH2SO4 / MWSO3)] / Maximum Boiler Heat Input (mmBtu/hr)
Total H2SO4 Emissions with SCR
SO2 Inlet (lb/mmBtu) | ----- | ----- | ----- | ----- | ----- | #REF! | [(Sulfur Content (%) / 100) x (MWSO2 / MWS) x 1,000,000 Btu/mmBtu] / Coal Heating Value (Btu/lb)
SO3 Boiler Outlet (lb/hr) | ----- | ----- | ----- | ----- | ----- | #REF! | Maximum Boiler Heat Input (mmBtu/hr) x SO2 Inlet (lb/mmBtu) x (CB / 100) x (MWSO3 / MWSO2)
SO3 Boiler Outlet (ppm) | ----- | ----- | ----- | ----- | ----- | #REF! | SO2 Inlet (lb/mmBtu) x (CB / 100) x CF
SO3 SCR Inlet (lb/hr) | ----- | ----- | ----- | ----- | ----- | #REF! | [SO3 SCR Inlet (ppm) / SO3 Boiler Outlet (ppm)] x SO3 Boiler Outlet (lb/hr)
SO3 SCR Inlet (ppm) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 Boiler Outlet (ppm) - CHESP (ppm)
SO3 SCR Outlet (lb/hr) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 SCR Inlet (lb/hr) + [SO2 Inlet (lb/mmBtu) x (CC / 100) x Boiler Heat Input (lb/hr) x (MWSO3 / MWSO2)]
SO3 SCR Outlet (ppm) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 SCR Inlet (ppm) + [SO2 Inlet (lb/mmBtu) x (CC / 100) x CF]
SO3 Air Preheater Outlet (lb/hr) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 SCR Outlet (lb/hr) x [1 - (CAPH / 100)]
SO3 Air Preheater Outlet (ppm) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 SCR Outlet (ppm) x [1 - (CAPH / 100)]
SO3 FGD Inlet (lb/hr) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 Air Preheater Outlet (lb/hr)
SO3 FGD Inlet (ppm) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 Air Preheater Outlet (ppm)
SO3 FGD Outlet (lb/hr) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 FGD Inlet (lb/hr) x [1 - (CFGD / 100)]
SO3 FGD Outlet (ppm) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 FGD Inlet (ppm) x [1 - (CFGD / 100)]
H2SO4 with SCR (tpy) | ----- | ----- | ----- | ----- | ----- | #REF! | SO3 FGD Outlet (lb/hr) x (MWH2SO4 / MWSO3) x Operating Hours (hr/yr) x (Capacity Factor (%) / 100) x (1 ton / 2,000 lb)
H2SO4 with SCR (lb/hr) | ----- | ----- | ----- | ----- | ----- | #REF! | [H2SO4 without SCR (tpy) x (2,000 lb / ton)] / Operating Hours (hr/yr)
H2SO4 with SCR (lb/mmBtu) | ----- | ----- | ----- | ----- | ----- | #REF! | [SO2 FGD Outlet (lb/hr) x (MWH2SO4 / MWSO3)] / Maximum Boiler Heat Input (mmBtu/hr)

## Emission Projections (hidden)
Table D-4
Unit 1 and Unit 2 - Emission Projections
Salt River Project - Coronado Generating Station
| Unit 1 | Unit 2
NOx (tpy) | #REF! | #REF!
SO2 (tpy) | #REF! | #REF!
Filterable PM (tpy) | #REF! | #REF!
Total PM10 (tpy) | #REF! | #REF!
H2SO4 (tpy) | #REF! | #REF!
CO (tpy) | #REF! | #REF!
VOC (tpy) | #REF! | #REF!
Mercury (tpy) | #REF! | #REF!
Capacity Factor
Capacity Factor (%) | 1 | 1
Post-Construction Emissions (tpy) = Post-Project Emissions (tpy) x Capacity Factor (%)

## Adjustment Projections (hidden)
Table D-5
Unit 1 and Unit 2 - Projection Adjustments
Salt River Project - Coronado Generating Station
| 2017 Post-Construction |  | 2018 Post-Construction |  | Notes
| Unit 1 | Unit 2 | Unit 1 | Unit 2
Unit Design Information
Design Gross Output (MW) | 456 | 456 | 456 | 456 | Engineering Assumption
Maximum Boiler Heat Input (mmBtu/hr) | 4719 | 4719 | 4719 | 4719 | Based on maximum capacity of unit
Boiler Heat Input (mmBtu/yr) | 41338440 | 41338440 | 41338440 | 41338440 | Maximum Boiler Heat Input (mmBtu/hr) x Operating Hours (hr/yr)
Operating Hours (hr/yr) | 8760 | 8760 | 8760 | 8760 | Assume 100% capacity factor
Coal Burned (tpy) | 2335505 | 2335505 | 2335505 | 2335505 | Engineering Assumption
Coal Burned (lbs/hr) | 533220.3196 | 533220.3196 | 533220.3196 | 533220.3196 | [Coal Burned (tpy) x 2,000 lb/ton] / Operating Hours (hr/yr)
Coal Heating Value (Btu/lb) | 8710 | 8710 | 8710 | 8710 | Engineering Assumption
Average Baseline Emission Factors
Baseline Filterable PM (lb/mmBtu) | 0.03 | 0.03 | 0.03 | 0.03 | Average emission factor from baseline emission calculations for 2005 and 2006
Baseline Total PM10 (lb/mmBtu) | 0.039551 | 0.039733 | 0.039724 | 0.039734 | Average emission factor from baseline emission calculations for 2005 and 2006
Baseline H2SO4 (lb/mmBtu) | 0.0045515 | 0.0047328 | 0.0047241 | 0.0047337 | Average emission factor from baseline emission calculations for 2005 and 2006
Baseline CO (lb/ton) | 0.5 | 0.5 | 0.5 | 0.5 | Average emission factor from baseline emission calculations for 2005 and 2006
Baseline VOC (lb/ton) | 0.06 | 0.06 | 0.06 | 0.06 | Average emission factor from baseline emission calculations for 2005 and 2006
Baseline Mercury (lb/mmBtu) | 8.3e-06 | 8.3e-06 | 8.3e-06 | 8.3e-06 | Average emission factor from baseline emission calculations for 2005 and 2006
Coal Emissions
NOx (tpy) | 0 | 0 | 0 | 0 | Did not evaluate projections due to emissions decrease
SO2 (tpy) | 0 | 0 | 0 | 0 | Did not evaluate projections due to emissions decrease
Filterable PM (tpy) | 552.5721 | 533.234 | 552.5721 | 533.234 | Baseline Filterable PM (lb/mmBtu) x Boiler Heat Input (mmBtu/yr) x (1 ton / 2,000 lb) x Capacity Factor (%)
Total PM10 (tpy) | 728.5017 | 706.2292 | 731.681 | 706.2448 | Baseline Total PM10 (lb/mmBtu) x Boiler Heat Input (mmBtu/yr) x (1 ton / 2,000 lb) x Capacity Factor (%)
H2SO4 (tpy) | 83.8342 | 84.1229 | 87.0135 | 84.1385 | Baseline H2SO4 (lb/mmBtu) x Boiler Heat Input (mmBtu/yr) x (1 ton / 2,000 lb) x Capacity Factor (%)
CO (tpy) | 520.3127 | 502.1035 | 520.3127 | 502.1035 | Baseline CO (lb/ton) x Coal Burned (tpy) x (1 ton / 2,000 lb) x Capacity Factor (%)
VOC (tpy) | 62.4375 | 60.2524 | 62.4375 | 60.2524 | Baseline VOC (lb/ton) x Coal Burned (tpy) x (1 ton / 2,000 lb) x Capacity Factor (%)
Mercury (tpy) | 0.15288 | 0.14753 | 0.15288 | 0.14753 | Baseline Mercury (lb/mmBtu) x Boiler Heat Input (mmBtu/yr) x (1 ton / 2,000 lb) x Capacity Factor (%)
Capacity Factor
Capacity Factor (%) | 0.89114 | 0.85995 | 0.89114 | 0.85995 | Resource Planning Assumption

## Boilers Actual to Actual (hidden)
Table D-6
Unit 1 and Unit 2 - Actual to Actual Emissions Increases
Salt River Project - Coronado Generating Station
Pollutant | Unit | Baseline Actuals (tpy) | Representative Actual Annual Emissions (w/o adjustments) (tpy) | Representative Actual Emissions with Demand Growth but without Project Increases (tpy) | Adjustment Amount (tpy) | Boilers Emissions Increase (tpy)
PM | Unit 1 | 519.5706 | #REF! | 552.5721 | 33.0015 | #REF!
PM | Unit 2 | 447.7949 | #REF! | 533.234 | 85.439 | #REF!
PM10 | Unit 1 | 685.036 | #REF! | 730.0913 | 45.0553 | #REF!
PM10 | Unit 2 | 593.071 | #REF! | 706.237 | 113.166 | #REF!
VOC | Unit 1 | 50.1446 | #REF! | 62.4375 | 12.2929 | #REF!
VOC | Unit 2 | 49.1525 | #REF! | 62.4375 | 13.2851 | #REF!
CO | Unit 1 | 417.8719 | #REF! | 520.3127 | 102.4408 | #REF!
CO | Unit 2 | 409.6037 | #REF! | 502.1035 | 92.4998 | #REF!
SO2 | Unit 1 | 6551.05 | #REF! | 0 | 0 | #REF!
SO2 | Unit 2 | 5444.9 | #REF! | 0 | 0 | #REF!
NOx | Unit 1 | 6903.0746 | #REF! | 0 | 0 | #REF!
NOx | Unit 2 | 6398.9865 | #REF! | 0 | 0 | #REF!
H2SO4 | Unit 1 | 77.9594 | #REF! | 85.4239 | 7.4644 | #REF!
H2SO4 | Unit 2 | 73.3981 | #REF! | 84.1307 | 10.7326 | #REF!
Mercury | Unit 1 | 0.14375 | #REF! | 0.15288 | 0.0091304 | #REF!
Mercury | Unit 2 | 0.12389 | #REF! | 0.14753 | 0.023638 | #REF!
Baseline Actuals (tpy) = [2005 Pre-Construction Emissions (tpy) + 2006 Pre-Construction Emissions (tpy)] / 2
Representative Actual Annual Emissions (w/o adjustments) (tpy) = [2017 Post-Construction Emissions (tpy) + 2018 Post-Construction Emissions (tpy)] / 2
Representative Actual Emissions with Demand Growth but without Project Increases (tpy) = [2017 Adjustment Projections (tpy) + 2018 Adjustment Projections (tpy)] / 2
Adjustment Amount = Representative Actual Emissions with Demand Growth but without Project Increases (tpy) - Baseline Actuals (tpy)
Boilers Emissions Increase (tpy) = Representative Actual Annual Emissions (w/o adjustments) (tpy) - Baseline Actuals (tpy) - Adjustment Amount (tpy)

## Material Handling Baseline (hidden)
Table D-7
Material Handling - Baseline Actual Emissions
Salt River Project - Coronado Generating Station
2002 Capacity Factor: |  | 0.736
2003 Capacity Factor: |  | 0.841
2004 Capacity Factor: |  | 0.84
2005 Capacity Factor: |  | 0.883
2006 Capacity Factor: |  | 0.856
Estimated Projected Particulate Matter Emissions from Material Handling Operations
[20 empty] | 2002 |  |  |  | 2003 |  |  |  | 2004 |  |  |  | 2005 |  |  |  | 2006
Source | Description | Max Throughput |  | 2002 Throughput |  | 2003 Throughput |  | 2004 Throughput |  | 2005 Throughput |  | 2006 Throughput |  | U (mph) | M (%) | PM10 EF (lb/ton) | PM EF | Emission | Control | PM10 Emissions |  | PM Emissions |  | PM10 Emissions |  | PM Emissions |  | PM10 Emissions |  | PM Emissions |  | PM10 Emissions |  | PM Emissions |  | PM10 Emissions |  | PM Emissions
ID |  | (tph) | (tpy) | (tph) | (tpy) | (tph) | (tpy) | (tph) | (tpy) | (tph) | (tpy) | (tph) | (tpy) |  |  |  | (lb/ton) | Control(s) | Efficiency | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr)
Coal Handling:
011 | Unloading | 1200 | 5000000 | 420.0913 | 3680000 | 1009.2 | 4205000 | 1008 | 4200000 | 1059.6 | 4415000 | 1027.2 | 4280000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | WS | 80% | 0.011162 | 0.048889 | 0.023599 | 0.10337 | 0.026814 | 0.055863 | 0.056693 | 0.11811 | 0.026783 | 0.055797 | 0.056626 | 0.11797 | 0.028154 | 0.058653 | 0.059525 | 0.12401 | 0.027293 | 0.05686 | 0.057705 | 0.12022
011 | Crushers | 1200 | 5000000 | 420.0913 | 3680000 | 1009.2 | 4205000 | 1008 | 4200000 | 1059.6 | 4415000 | 1027.2 | 4280000 | --- | --- | 0.00054 | 0.0012 | DC | 99% | 0.0022685 | 0.009936 | 0.0050411 | 0.02208 | 0.0054497 | 0.011354 | 0.01211 | 0.02523 | 0.0054432 | 0.01134 | 0.012096 | 0.0252 | 0.0057218 | 0.011921 | 0.012715 | 0.02649 | 0.0055469 | 0.011556 | 0.012326 | 0.02568
011 | BC-2A | 1500 | 5000000 | 420.0913 | 3680000 | 1261.5 | 4205000 | 1260 | 4200000 | 1324.5 | 4415000 | 1284 | 4280000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | WS | 80% | 0.011162 | 0.048889 | 0.023599 | 0.10337 | 0.033518 | 0.055863 | 0.070867 | 0.11811 | 0.033478 | 0.055797 | 0.070783 | 0.11797 | 0.035192 | 0.058653 | 0.074406 | 0.12401 | 0.034116 | 0.05686 | 0.072131 | 0.12022
011 | BC-3A | 3000 | 2500000 | 210.0457 | 1840000 | 2523 | 2102500 | 2520 | 2100000 | 2649 | 2207500 | 2568 | 2140000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | WS | 80% | 0.0055809 | 0.024444 | 0.0118 | 0.051683 | 0.067036 | 0.027932 | 0.14173 | 0.059056 | 0.066956 | 0.027899 | 0.14157 | 0.058985 | 0.070384 | 0.029327 | 0.14881 | 0.062005 | 0.068232 | 0.02843 | 0.14426 | 0.060109
011 | BC-3B | 1200 | 2500000 | 210.0457 | 1840000 | 1009.2 | 2102500 | 1008 | 2100000 | 1059.6 | 2207500 | 1027.2 | 2140000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | Fog | 99% | 0.00027905 | 0.0012222 | 0.00058998 | 0.0025841 | 0.0013407 | 0.0013966 | 0.0028347 | 0.0029528 | 0.0013391 | 0.0013949 | 0.0028313 | 0.0029493 | 0.0014077 | 0.0014663 | 0.0029762 | 0.0031002 | 0.0013646 | 0.0014215 | 0.0028852 | 0.0030055
011 | BC-3C | 1200 | 2500000 | 210.0457 | 1840000 | 1009.2 | 2102500 | 1008 | 2100000 | 1059.6 | 2207500 | 1027.2 | 2140000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0.00027905 | 0.0012222 | 0.00058998 | 0.0025841 | 0.0013407 | 0.0013966 | 0.0028347 | 0.0029528 | 0.0013391 | 0.0013949 | 0.0028313 | 0.0029493 | 0.0014077 | 0.0014663 | 0.0029762 | 0.0031002 | 0.0013646 | 0.0014215 | 0.0028852 | 0.0030055
011 | BC-4 | 3000 | 2500000 | 210.0457 | 1840000 | 2523 | 2102500 | 2520 | 2100000 | 2649 | 2207500 | 2568 | 2140000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | WS | 80% | 0.0055809 | 0.024444 | 0.0118 | 0.051683 | 0.067036 | 0.027932 | 0.14173 | 0.059056 | 0.066956 | 0.027899 | 0.14157 | 0.058985 | 0.070384 | 0.029327 | 0.14881 | 0.062005 | 0.068232 | 0.02843 | 0.14426 | 0.060109
011 | Stacker | 3000 | 2500000 | 210.0457 | 1840000 | 2523 | 2102500 | 2520 | 2100000 | 2649 | 2207500 | 2568 | 2140000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | WS | 80% | 0.0055809 | 0.024444 | 0.0118 | 0.051683 | 0.067036 | 0.027932 | 0.14173 | 0.059056 | 0.066956 | 0.027899 | 0.14157 | 0.058985 | 0.070384 | 0.029327 | 0.14881 | 0.062005 | 0.068232 | 0.02843 | 0.14426 | 0.060109
011 | BC-5 | 1200 | 5000000 | 420.0913 | 3680000 | 1009.2 | 4205000 | 1008 | 4200000 | 1059.6 | 4415000 | 1027.2 | 4280000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | WS, DC | 99% | 0.00055809 | 0.0024444 | 0.00118 | 0.0051683 | 0.0013407 | 0.0027932 | 0.0028347 | 0.0059056 | 0.0013391 | 0.0027899 | 0.0028313 | 0.0058985 | 0.0014077 | 0.0029327 | 0.0029762 | 0.0062005 | 0.0013646 | 0.002843 | 0.0028852 | 0.0060109
011 | BC-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
011 | BC-7A | 1200 | 2500000 | 210.0457 | 1840000 | 1009.2 | 2102500 | 1008 | 2100000 | 1059.6 | 2207500 | 1027.2 | 2140000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | Fog | 99% | 0.00027905 | 0.0012222 | 0.00058998 | 0.0025841 | 0.0013407 | 0.0013966 | 0.0028347 | 0.0029528 | 0.0013391 | 0.0013949 | 0.0028313 | 0.0029493 | 0.0014077 | 0.0014663 | 0.0029762 | 0.0031002 | 0.0013646 | 0.0014215 | 0.0028852 | 0.0030055
011 | BC-7B | 1200 | 2500000 | 210.0457 | 1840000 | 1009.2 | 2102500 | 1008 | 2100000 | 1059.6 | 2207500 | 1027.2 | 2140000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0.00027905 | 0.0012222 | 0.00058998 | 0.0025841 | 0.0013407 | 0.0013966 | 0.0028347 | 0.0029528 | 0.0013391 | 0.0013949 | 0.0028313 | 0.0029493 | 0.0014077 | 0.0014663 | 0.0029762 | 0.0031002 | 0.0013646 | 0.0014215 | 0.0028852 | 0.0030055
011 | BC-8A | 1201 | 1250000 | 105.0228 | 920000 | 1010.041 | 1051250 | 1008.84 | 1050000 | 1060.483 | 1103750 | 1028.056 | 1070000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0.00013952 | 0.00061111 | 0.00029499 | 0.0012921 | 0.0013418 | 0.00069829 | 0.002837 | 0.0014764 | 0.0013402 | 0.00069746 | 0.0028337 | 0.0014746 | 0.0014089 | 0.00073317 | 0.0029787 | 0.0015501 | 0.0013658 | 0.00071075 | 0.0028876 | 0.0015027
011 | BC-8B | 1202 | 1250000 | 105.0228 | 920000 | 1010.882 | 1051250 | 1009.68 | 1050000 | 1061.366 | 1103750 | 1028.912 | 1070000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0.00013952 | 0.00061111 | 0.00029499 | 0.0012921 | 0.001343 | 0.00069829 | 0.0028394 | 0.0014764 | 0.0013414 | 0.00069746 | 0.002836 | 0.0014746 | 0.00141 | 0.00073317 | 0.0029812 | 0.0015501 | 0.0013669 | 0.00071075 | 0.00289 | 0.0015027
011 | BC-9A | 1203 | 1250000 | 105.0228 | 920000 | 1011.723 | 1051250 | 1010.52 | 1050000 | 1062.249 | 1103750 | 1029.768 | 1070000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0.00013952 | 0.00061111 | 0.00029499 | 0.0012921 | 0.0013441 | 0.00069829 | 0.0028418 | 0.0014764 | 0.0013425 | 0.00069746 | 0.0028384 | 0.0014746 | 0.0014112 | 0.00073317 | 0.0029837 | 0.0015501 | 0.001368 | 0.00071075 | 0.0028924 | 0.0015027
011 | BC-9B | 1204 | 1250000 | 105.0228 | 920000 | 1012.564 | 1051250 | 1011.36 | 1050000 | 1063.132 | 1103750 | 1030.624 | 1070000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0.00013952 | 0.00061111 | 0.00029499 | 0.0012921 | 0.0013452 | 0.00069829 | 0.0028441 | 0.0014764 | 0.0013436 | 0.00069746 | 0.0028407 | 0.0014746 | 0.0014124 | 0.00073317 | 0.0029862 | 0.0015501 | 0.0013692 | 0.00071075 | 0.0028948 | 0.0015027
011 | BC-10A | 1205 | 1250000 | 105.0228 | 920000 | 1013.405 | 1051250 | 1012.2 | 1050000 | 1064.015 | 1103750 | 1031.48 | 1070000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0.00013952 | 0.00061111 | 0.00029499 | 0.0012921 | 0.0013463 | 0.00069829 | 0.0028465 | 0.0014764 | 0.0013447 | 0.00069746 | 0.0028431 | 0.0014746 | 0.0014135 | 0.00073317 | 0.0029886 | 0.0015501 | 0.0013703 | 0.00071075 | 0.0028973 | 0.0015027
011 | BC-10B | 1206 | 1250000 | 105.0228 | 920000 | 1014.246 | 1051250 | 1013.04 | 1050000 | 1064.898 | 1103750 | 1032.336 | 1070000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC | 99% | 0.00013952 | 0.00061111 | 0.00029499 | 0.0012921 | 0.0013474 | 0.00069829 | 0.0028488 | 0.0014764 | 0.0013458 | 0.00069746 | 0.0028455 | 0.0014746 | 0.0014147 | 0.00073317 | 0.0029911 | 0.0015501 | 0.0013715 | 0.00071075 | 0.0028997 | 0.0015027
011 | Coal Silos | 1200 | 5000000 | 420.0913 | 3680000 | 1009.2 | 4205000 | 1008 | 4200000 | 1059.6 | 4415000 | 1027.2 | 4280000 | 8.8 | 15.5 | 0.00013285 | 0.00028088 | DC, SC | 99% | 0.00055809 | 0.0024444 | 0.00118 | 0.0051683 | 0.0013407 | 0.0027932 | 0.0028347 | 0.0059056 | 0.0013391 | 0.0027899 | 0.0028313 | 0.0058985 | 0.0014077 | 0.0029327 | 0.0029762 | 0.0062005 | 0.0013646 | 0.002843 | 0.0028852 | 0.0060109
[20 empty] | 0.044404 | 0.19449 | 0.094129 | 0.41228 | 0.283 | 0.22224 | 0.59894 | 0.4711 | 0.28267 | 0.22197 | 0.59823 | 0.47054 | 0.29714 | 0.23334 | 0.62885 | 0.49463 | 0.28805 | 0.2262 | 0.60962 | 0.4795
Limestone Handling:
007 | Bucket Elevator - TP8 | 22 | 192720 | 16.192 | 141841.92 | 18.502 | 162077.52 | 18.48 | 161884.8 | 19.426 | 170171.76 | 18.832 | 164968.32 | 8.8 | 2.1 | 0.0021813 | 0.0046119 | DC | 99% | 0.0003532 | 0.001547 | 0.00074676 | 0.0032708 | 0.00040359 | 0.0017677 | 0.0008533 | 0.0037375 | 0.00040311 | 0.0017656 | 0.00085229 | 0.003733 | 0.00042374 | 0.001856 | 0.00089591 | 0.0039241 | 0.00041079 | 0.0017992 | 0.00086852 | 0.0038041
007 | Slide Gate Feeders | 44 | 96360 | 32.384 | 70920.96 | 37.004 | 81038.76 | 36.96 | 80942.4 | 38.852 | 85085.88 | 37.664 | 82484.16 | 8.8 | 2.1 | 0.0021813 | 0.0046119 | -- | -- | 0.07064 | 0.077351 | 0.14935 | 0.16354 | 0.080718 | 0.088386 | 0.17066 | 0.18687 | 0.080622 | 0.088281 | 0.17046 | 0.18665 | 0.084749 | 0.0928 | 0.17918 | 0.19621 | 0.082157 | 0.089962 | 0.1737 | 0.19021
007 | BC-102 | 22 | 48180 | 16.192 | 35460.48 | 18.502 | 40519.38 | 18.48 | 40471.2 | 19.426 | 42542.94 | 18.832 | 41242.08 | 8.8 | 2.1 | 0.0021813 | 0.0046119 | -- | -- | 0.03532 | 0.038675 | 0.074676 | 0.1111 | 0.040359 | 0.71557 | 0.08533 | 0.093436 | 0.78401 | 0.04414 | 0.085229 | 0.093325 | 0.042374 | 0.0464 | 0.089591 | 0.098103 | 0.041079 | 0.044981 | 0.086852 | 0.095103
007 | Crushers | 44 | 96360 | 32.384 | 70920.96 | 37.004 | 81038.76 | 36.96 | 80942.4 | 38.852 | 85085.88 | 37.664 | 82484.16 | --- | --- | 0.00054 | 0.0012 | DC | 99% | 0.00017487 | 0.00019149 | 0.00038861 | 0.00057816 | 0.00019982 | 0.0002188 | 0.00044405 | 0.00048623 | 0.00019958 | 0.00021854 | 0.00044352 | 0.00048565 | 0.0002098 | 0.00022973 | 0.00046622 | 0.00051052 | 0.00020339 | 0.00022271 | 0.00045197 | 0.0004949
007 | BC-103 | 22 | 48180 | 16.192 | 35460.48 | 18.502 | 40519.38 | 18.48 | 40471.2 | 19.426 | 42542.94 | 18.832 | 41242.08 | 8.8 | 2.1 | 0.0021813 | 0.0046119 | -- | -- | 0.03532 | 0.038675 | 0.074676 | 0.081771 | 0.040359 | 0.044193 | 0.08533 | 0.093436 | 0.040311 | 0.04414 | 0.085229 | 0.093325 | 0.042374 | 0.0464 | 0.089591 | 0.098103 | 0.041079 | 0.044981 | 0.086852 | 0.095103
[20 empty] | 0.14181 | 0.15644 | 0.29984 | 0.36026 | 0.16204 | 0.85014 | 0.34262 | 0.37797 | 0.90554 | 0.17855 | 0.34221 | 0.37752 | 0.17013 | 0.18769 | 0.35973 | 0.39685 | 0.16493 | 0.18195 | 0.34873 | 0.38471
Fly Ash Handling:
012 | Ash Loading | 88 | 770880 | 64.768 | 567367.68 | 74.008 | 648310.08 | 73.92 | 647539.2 | 77.704 | 680687.04 | 75.328 | 659873.28 | 8.8 | 27 | 6.1083e-05 | 0.00012915 | DC | 99% | 3.9562e-05 | 0.00017328 | 8.3645e-05 | 0.00036637 | 4.5206e-05 | 0.000198 | 9.5578e-05 | 0.00041863 | 4.5152e-05 | 0.00019777 | 9.5465e-05 | 0.00041814 | 4.7464e-05 | 0.00020789 | 0.00010035 | 0.00043954 | 4.6012e-05 | 0.00020153 | 9.7283e-05 | 0.0004261
012 | Ash Unloading | 59 | 516840 | 43.424 | 380394.24 | 49.619 | 434662.44 | 49.56 | 434145.6 | 52.097 | 456369.72 | 50.504 | 442415.04 | 8.8 | 27 | 6.1083e-05 | 0.00012915 | DC | 99% | 2.6524e-05 | 0.00011618 | 5.608e-05 | 0.00024563 | 3.0309e-05 | 0.00013275 | 6.4081e-05 | 0.00028067 | 3.0273e-05 | 0.00013259 | 6.4005e-05 | 0.00028034 | 3.1822e-05 | 0.00013938 | 6.7281e-05 | 0.00029469 | 3.0849e-05 | 0.00013512 | 6.5224e-05 | 0.00028568
[20 empty] | 6.6086e-05 | 0.00028946 | 0.00013973 | 0.000612 | 7.5515e-05 | 0.00033075 | 0.00015966 | 0.00069931 | 7.5425e-05 | 0.00033036 | 0.00015947 | 0.00069848 | 7.9286e-05 | 0.00034727 | 0.00016763 | 0.00073423 | 7.6861e-05 | 0.00033665 | 0.00016251 | 0.00071178
TOTAL | [19 empty] | 0.18628 | 0.35122 | 0.39411 | 0.77316 | 0.44512 | 1.0727 | 0.94171 | 0.84977 | 1.1883 | 0.40085 | 0.94059 | 0.84876 | 0.46735 | 0.42137 | 0.98874 | 0.89221 | 0.45306 | 0.40849 | 0.95851 | 0.86493
NOTES:
1) Emissions from transfer points based on AP-42, Equation (1) and Table 13.2.4.1 (11/06).
2) Annual average wind speed of 8.8 mph based on Winslow data from NCDC.
3) Emissions from crushers based on AP-42, Table 11.19.2-2 (8/04), using controlled emission factors.
4) Assume PM10 emissions are 27% of PM, based on SRP Title V Renewal Calculations.
5) TP = Transfer Point, WS = Wet Suppression. DC = Dust Collector; VBF = Vent Bag Filter; FS = Filter Separator; SC = Wet Scrubber..
6) Fog control efficiency from fog vendor website.
7) Controlled Emissions (lb/hr) = Throughput (ton/hr) x Emission Factor (lb/ton) x (100% - Control Efficiency)
8) Annual capacity factors are an average of the annual capacity factors for Units 1 and 2.

## Mat Hand Pt Source Baseline (hidden)
Table D-8
Material Handling Point Sources - Baseline Actual Emissions
Salt River Project - Coronado Generating Station
2002 Capacity Factor: |  | 0.736
2003 Capacity Factor: |  | 0.841
2004 Capacity Factor: |  | 0.84
2005 Capacity Factor: |  | 0.883
2006 Capacity Factor: |  | 0.856
Estimated PM10 Emissions from Material Handling Control Devices | [5 empty] | 2002 |  | 2003 |  | 2004 |  | 2005 |  | 2006
Source ID | Emission Point | Description | Control | Flow Rate (acfm) | EF (gr/acf) | Emissions |  | Emissions |  | Emissions |  | Emissions |  | Emissions
|  |  | Device |  |  | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr)
Coal Handling:
011 | DC-2 | Coal Crusher House | Baghouse | 16200 | 0.01 | 1.022 | 4.4763 | 1.1678 | 5.1149 | 1.1664 | 5.1088 | 1.2261 | 5.3704 | 1.1886 | 5.2061
011 | DC-3 | Coal Transfer Area U1 | Baghouse | 18000 | 0.01 | 1.1355 | 4.9737 | 1.2975 | 5.6832 | 1.296 | 5.6765 | 1.3623 | 5.9671 | 1.3207 | 5.7846
011 | DC-4 | Coal Transfer Area U2 | Baghouse | 12000 | 0.01 | 0.75703 | 3.3158 | 0.86503 | 3.7888 | 0.864 | 3.7843 | 0.90823 | 3.978 | 0.88046 | 3.8564
011 | DC-5A | Coal Silo 1 | Baghouse | 2000 | 0.01 | 0.12617 | 0.55263 | 0.14417 | 0.63147 | 0.144 | 0.63072 | 0.15137 | 0.66301 | 0.14674 | 0.64273
011 | DC-5B | Coal Silo 2 | Baghouse | 2000 | 0.01 | 0.12617 | 0.55263 | 0.14417 | 0.63147 | 0.144 | 0.63072 | 0.15137 | 0.66301 | 0.14674 | 0.64273
011 | DC-5C | Coal Silo 3 | Baghouse | 2000 | 0.01 | 0.12617 | 0.55263 | 0.14417 | 0.63147 | 0.144 | 0.63072 | 0.15137 | 0.66301 | 0.14674 | 0.64273
011 | DC-5D | Coal Silo 4 | Wet Scrubbing | 2000 | 0.01 | 0.12617 | 0.55263 | 0.14417 | 0.63147 | 0.144 | 0.63072 | 0.15137 | 0.66301 | 0.14674 | 0.64273
011 | DC-5E | Coal Silo 5 | Wet Scrubbing | 2000 | 0.01 | 0.12617 | 0.55263 | 0.14417 | 0.63147 | 0.144 | 0.63072 | 0.15137 | 0.66301 | 0.14674 | 0.64273
011 | DC-5F | Coal Silo 6 | Wet Scrubbing | 2000 | 0.01 | 0.12617 | 0.55263 | 0.14417 | 0.63147 | 0.144 | 0.63072 | 0.15137 | 0.66301 | 0.14674 | 0.64273
011 | DC-6 | Coal Sample Building Ext. | Baghouse | 15000 | 0.01 | 0.94629 | 4.1447 | 1.0813 | 4.736 | 1.08 | 4.7304 | 1.1353 | 4.9726 | 1.1006 | 4.8205
011 | DC-7A | Fly Ash Bin Vent 1 | Baghouse | 2375 | 0.01 | 0.14983 | 0.65625 | 0.1712 | 0.74987 | 0.171 | 0.74898 | 0.17975 | 0.78732 | 0.17426 | 0.76325
011 | DC-7B | Fly Ash Bin Vent 2 | Baghouse | 2375 | 0.01 | 0.14983 | 0.65625 | 0.1712 | 0.74987 | 0.171 | 0.74898 | 0.17975 | 0.78732 | 0.17426 | 0.76325
011 | DC-8 | Fly Ash Receiving Silos | Baghouse | 15000 | 0.01 | 0.94629 | 4.1447 | 1.0813 | 4.736 | 1.08 | 4.7304 | 1.1353 | 4.9726 | 1.1006 | 4.8205
[6 empty] | 5.8638 | 25.6835 | 6.7004 | 29.3476 | 6.6924 | 29.3127 | 7.035 | 30.8132 | 6.8199 | 29.871
Limestone Handling:
007 | DC-9 | Limestone Ball Mill | Baghouse | 7000 | 0.01 | 0.4416 | 1.9342 | 0.5046 | 2.2101 | 0.504 | 2.2075 | 0.5298 | 2.3205 | 0.5136 | 2.2496
007 | DC-10 | Soda Ash | Baghouse | 300 | 0.01 | 0.018926 | 0.082895 | 0.021626 | 0.094721 | 0.0216 | 0.094608 | 0.022706 | 0.099451 | 0.022011 | 0.09641
007 | DC-11 | Lime | Baghouse | 300 | 0.01 | 0.018926 | 0.082895 | 0.021626 | 0.094721 | 0.0216 | 0.094608 | 0.022706 | 0.099451 | 0.022011 | 0.09641
[6 empty] | 0.47945 | 2.1 | 0.54785 | 2.3996 | 0.5472 | 2.3967 | 0.57521 | 2.5194 | 0.55762 | 2.4424
TOTAL | [5 empty] | 6.3433 | 27.7835 | 7.2482 | 31.7472 | 7.2396 | 31.7094 | 7.6102 | 33.3327 | 7.3775 | 32.3134
Notes:
1) Emission factors based on manufacturers' data.
2) DC = Dust Collector; VBF = Vent Bag Filter; FS = Filter Separator.
3) Emission Rates determined by: Emissions (lb/hr) = flow rate (acfm) x emission factor (gr/acf) x (lb/7000 grain) x (hr/60 min)
4) DC-5D,E, and F have been changed from baghouses to wet scrubbing devices.
5) Annual capacity factors are an average of the annual capacity factors for Units 1 and 2.

## Instructions
The "Emission Factors" and "Emission Calculations" spreadsheets are template guides provided to facilities for submitting emission calculations in an electronic format. Submitting the calculations electronically will aid the Department in processing permit applications. Please note that the templates are only a suggestion, and all listed values and calculations are examples which can be amended to meet your specific requirements. Rows and columns may be added, deleted, and resized as necessary. Facilities with emissions of greenhouse gases, lead, or HAPs can copy the "Emission Calcs" spreadsheet tab and modify the pollutant headings as necessary.
Below are brief descriptions of the fields required:
EMISSION FACTORS TAB |  | EXAMPLE
Emissions ID | Input the Equipment ID or the process number for which emission calculations are made | Process #5
Description | Describe the equipment or process | truck loading with front end loader
Pollutants | List each pollutant emitted from the process (one per line) | PM
PM10
PM2.5
Emissions Factor (EF) | List the emission factor for each pollutant | PM = 8.34E-04
PM10 = 3.94E-04
PM2.5 = 5.97E-05
EF Units | List the units of the emission factors | lb/ton
EF Equation | List the equation, if any, that was used to develop the factor | EF = k*0.0032*(((U/5)^1.3)/((M/2)^1.4))
EF Inputs | List the equation and the corresponding parameter and inputs variables alogn with the units. If there are no equations, this cell can be left blank | PM: k = 0.74 (dimensionless)
PM10: k = 0.35 (dimensionless)
PM2.5 k = 0.053 (dimensionless)
U = 6.4 mph
M = 5.3%
References/Comments | Cite the source, reference, or derivation of all emission factors, equations and variables. If referenced value is from a source other than a commonly recognizable source, (e.g. AP42, EPA or ADEQ Guidance) provide a web link or copy of the source. | AP42 13.2.4 Equation 1 (11/06)
Wind speed: WRCC* annual average for Flagstaff, 1986-2011 * http://www.wrcc.dri.edu/summary/flg.az.html
Moisture content: facility ore assay lab
EMISSION CALCULATIONS TAB |  | EXAMPLE
Emission Source Identification (ID) & Description: | Input the Equipment ID or a process identification number for which emission calculations are made | GEN01
| Input the description of the equipment, fuel used, if any, and type of control used | Emergency Generator
N/A, diesel, natural gas, etc.
None, baghouse, SCR, etc.
HOURLY Maximum Capacity/ Process Rate | Input the maximum rated capacity or hourly process rate | 1105
Units | Input the units of max capacity or note process rate units per hour | horsepower, tons per hour, etc.
Pollutant | Link these cells to the appropriate data in the "Emission Factor Details" sheet, or transfer the information
Emission Factor
Emission Factor Units
Control Efficiency | Input the efficiency of the control device | na, 95%, maximum 0.7 g/hp-hr, etc.
Control Efficiency Basis (far right column) | Cite the justification for the control efficiency | manufacturers performance specification, AP42 Section 13.2.2.3
Emissions | Enter the emission calculation in units of pounds per hour, use one line for each pollutant | 7750
ANNUAL Maximum Capacity/ Process Rate | Input the maximum rated capacity or annual process rate | 500
Units | Input the units of max capacity or note process rate units per year | horsepower, tons per year, etc.
Derivation | Note how hourly emissions are converted to annual, or the opposite if that is the case | hourly × 8760 hr/yr, operation limited to 5 days per week, etc.

## Emission Factors
Emission ID | Description | Pollutant | EF | EF (Units) | EF Inputs |  |  |  | References/Comments
[5 empty] | EF Equation | Parameter | Value | Units
#5 | truck loading from front end loader | PM | 0.00083409 | lb/ton | EF = k*0.0032*(((U/5)^1.3)/((M/2)^1.4)) | k | 0.74 | none | AP42 13.2.4 Equation 1 (11/06)
[6 empty] | U | 6.4 | mph | see note 1
[6 empty] | M | 5.3 | % | see note 2
|  | PM10 | 0.0003945 | lb/ton | EF = k*0.0032*(((U/5)^1.3)/((M/2)^1.4)) | k | 0.35 | none | AP42 13.2.4 Equation 1 (11/06)
[6 empty] | U | 6.4 | mph | see note 1
[6 empty] | M | 5.3 | % | see note 2
|  | PM2.5 | 5.9739e-05 | lb/ton | EF = k*0.0032*(((U/5)^1.3)/((M/2)^1.4)) | k | 0.053 | none | AP42 13.2.4 Equation 1 (11/06)
[6 empty] | U | 6.4 | mph | see note 1
[6 empty] | M | 5.3 | % | see note 2
GEN01 | emergency generator | PM, PM10 & PM2.5 | 0.02 | g/hp-hr | not appplicable |  |  |  | manufacturer's specifications
|  | CO | 0.27 | g/hp-hr
|  | NOx | 4.61 | g/hp-hr
|  | VOC | 0.03 | g/hp-hr
|  | SOx | 0.011225 | lb/hr | EF = 52.7*7.1*0.000015*2.00 | BSFC | 52.7 | gal/hr | Mfg BSFC and 0.0015% fuel sulfur
[6 empty] | fuel density | 7.1 | lb/gal
[6 empty] | S content | 0.0015 | %
[6 empty] | S to SO2 | 2 | ratio
Notes:
1 | Wind speed: WRCC annual average for Flagstaff, 1986-2011 (http://www.wrcc.dri.edu/summary/flg.az.html)
2 | facility ore assay lab, see detail in section xxx of application

## Emission Calcs
Emission Source |  | HOURLY Maximum Capacity / Process Rate | Units | Pollutant | Emission Factor | Emission Factor Units | Control Efficiency | Emissions (lb/hour) | [6 empty] | Control Efficiency Basis
ID | Description | [6 empty] | PM | PM10 | PM2.5 | NOx | CO | SO2 | VOC
#5 | Material handling, truck loading by front end loader, water spray control | 2300 | tons/hr | PM | 0.00083409 | lb/ton | 80% | 0.38368 | [6 empty] | AP42 Section 13.2.2.3
|  |  |  | PM10 | 0.0003945 | lb/ton | 80% |  | 0.18147 | [5 empty] | AP42 Section 13.2.2.3
|  |  |  | PM2.5 | 5.9739e-05 | lb/ton | 80% |  |  | 0.02748 |  |  |  |  | AP42 Section 13.2.2.3
GEN01 | Fuel burning equipment, emergency generator, diesel fired | 1105 | hp | PM, PM10 & PM2.5 | 0.02 | g/hp-hr | na | 0.048721 | 0.048721 | 0.048721
|  |  |  | NOx | 4.61 | g/hp-hr | na |  |  |  | 11.2303
|  |  |  | CO | 0.27 | g/hp-hr | na |  |  |  |  | 0.65774
|  |  |  | VOC | 0.03 | g/hp-hr | na | [6 empty] | 0.073082
|  |  |  | SO2 | 0.011225 | lb/hr | na | [5 empty] | 0.011225
Emission Source |  | ANNUAL Maximum Capacity / Process Rate | Units | Pollutant | Emission Factor | Emission Factor Units | Control Efficiency | Emissions (ton/year) | [6 empty] | Indicate how annual emissions were calculated from hourly emissions (or the opposite, if that is the case)
ID | Description | [6 empty] | PM | PM10 | PM2.5 | NOx | CO | SO2 | VOC
#5 | truck loading from front end loader | 20148000 | tons/yr | PM | 0.00083409 | lb/ton | 80% | 1.6805 | [6 empty] | Based on annual capacity and 8760 hours per year
|  |  |  | PM10 | 0.0003945 | lb/ton | 80% |  | 0.79484
|  |  |  | PM2.5 | 5.9739e-05 | lb/ton | 80% |  |  | 0.12036
GEN01 | emergency generator | 500 | hr/year | PM, PM10 & PM2.5 | 0.02 | g/hp-hr | na | 0.01218 | 0.01218 | 0.01218 |  |  |  |  | Use of 500 hours per year for Emergency Engines
|  |  |  | NOx | 4.61 | g/hp-hr | na |  |  |  | 2.8076
|  |  |  | CO | 0.27 | g/hp-hr | na |  |  |  |  | 0.16443
|  |  |  | VOC | 0.03 | g/hp-hr | na | [6 empty] | 0.018271
|  |  |  | SO2 | 0.011225 | lb/hr | na | [5 empty] | 0.0028063

## Mat Handling Actual to Actual (hidden)
Table D-11
Material Handling - Actual to Actual Emissions Increases
Salt River Project - Coronado Generating Station
Pollutant | Baseline Actuals (tons/yr) | Representative Actual Annual Emissions (w/o adjustments) (tons/yr) | Representative Actual Emissions with Demand Growth but without Project Increases (tons/yr) | Adjustment Amount (demand growth) (tons/yr) | Representative Actual Annual Emissions without Demand Growth (tons/yr) | Emissions Increase (tons/yr)
PM10 | 33.238 | #REF! | 35.4241 | 2.1861 | #REF! | #REF!
PM | 33.7016 | #REF! | 35.8422 | 2.1406 | #REF! | #REF!
1) Baseline actual material handling emissions comprise point source and fugitive emissions from
coal handling, limestone handling, and fly ash handling.
2) Representative actual emissions comprise point source and fugitive emissions from
coal handling, limestone handling, fly ash handling, and bottom ash handling.
Baseline Actuals (tpy) = [(2005 Material Handling Baseline Actual Emissions (tpy) + 2006 Material Handling Baseline Actual Emissions (tpy)) / 2] +
[(2005 Material Handling Point Source Baseline Actual Emissions (tpy) + 2006 Material Handling Point Source Baseline Actual Emissions (tpy)) / 2]
Representative Actual Annual Emissions (w/o adjustments) (tpy) = [(2017 Material Handling Projected Actual Emissions (tpy) + 2018 Material Handling Projected Actual Emissions (tpy)) / 2] +
[(2017 Material Handling Point Source Projected Actual Emissions (tpy) + 2018 Material Handling Point Source Projected Actual Emissions (tpy)) / 2]
Representative Actual Emissions with Demand Growth but without Project Increases (tpy) = Baseline Actuals (tpy) x
[Boiler Actual to Actual Representative Actual Annual Emis without Demand Growth / Boiler Actual to Actual Representative Actual Annual Emis w/o Adjustments]
Adjustment Amount = Representative Actual Emissions with Demand Growth but without Project Increases (tpy) - Baseline Actuals (tpy)
Emissions Increase (tpy) = Representative Actual Annual Emissions (w/o adjustments) (tpy) - Baseline Actuals (tpy) - Adjustment Amount (tpy)

## Hauling Baseline (hidden)
Table D-12
Hauling - Baseline Actual Emissions
Salt River Project - Coronado Generating Station
Estimated PM Emissions from Vehicular Traffic and Off-Road Machinery | [10 empty] | 2005 |  | 2006
Source ID | Haul Road Description | Vehicle | Rate (VMT/yr) | s (%) | S (mph) | W (tons) | P (# of days) | PM10 EF (lb/VMT) | PM EF (lb/VMT) | Control (%) | PM10 Emissions (tons/yr) | PM Emissions (tons/yr) | PM10 Emissions (tons/yr) | PM Emissions (tons/yr)
010 | Fly Ash Disposal | Haul Truck | 1336.335 | 6.4 | 15 | 73.8 | 65 | 2.959 | 10.9609 | 80% | 0.39542 | 1.4647 | 0.39542 | 1.4647
010 | Bottom Ash Disposal | Haul Truck | 2134.665 | 6.4 | 15 | 73.8 | 65 | 2.959 | 10.9609 | 80% | 0.63164 | 2.3398 | 0.63164 | 2.3398
010 | Limestone Delivery | Dump Truck | 2308.2386 | 6.4 | 15 | 73.8 | 65 | 2.959 | 10.9609 | 80% | 0.683 | 2.53 | 0.683 | 2.53
|  | Vehicle | Rate (hrs/yr) | s (%) | M (%) | --- | -- | PM10 EF (lb/hr) | PM EF (lb/hr) | --- | PM10 Emissions (tons/yr) | PM Emissions (tons/yr) | PM10 Emissions (tons/yr) | PM Emissions (tons/yr)
010 | Coal Moving | Bulldozers | 4000 | 8.6 | 10.4 | --- | -- | 13.2579 | 49.3822 | --- | 26.5158 | 98.7645 | 26.5158 | 98.7645
[11 empty] | 28.2259 | 105.099 | 28.2259 | 105.099
Notes:
1) Truck emissions based on AP-42, equation (1a), with constants from Table 13.2.2-2 and 13.2.2-3 (11/06).
2) Number of days of precipitation for truck emissions based on AP-42, Figure 13.2.2-1 (11/06)
and equation 13.2.2-7 (11/06).
3) Bulldozer emissions based on AP-42, Table 11.9-1 (bulldozing coal), (<15um) (10/98).
4) Vehicle weight is average of empty and full vehicle weights.
5) Emissions from water trucks, service vehicles, employee vehicles, and other small truck traffic is trivial.
6) Control system using water spray.
7) Vehicle miles traveled estimated from SRP Haul Path Drawings, File Nos. CSK-TR-1 through CSK-TR-6.
8) VMT = Vehicle Miles Traveled; S = Speed; W = Mean Vehicle Weight; M = Moisture Content; P=Number of days with measurable precipitation
9) Control efficiencies from Reasonably Available Control Measures for Fugitive Dust, Section 2.1 General Fugitive Dust Emission Sources. Environmental Protection Agency, Ohio
10) Annual capacity factors are an average of the annual capacity factors for Units 1 and 2.
11) Bottom ash and fly ash disposal emissions estimated assuming each of the large, medium
and small haul trucks makes 1/3 of the total trips.
12) VMT calculated using total vehicle miles and weight fraction of bottom and fly ash hauled. Total ash hauled consists of 38.5% fly ash and 61.5 % bottom ash.
13) Limestone truck VMT based on total of 30,000 tpy of limestone usage and 16 ton per truck delivered per trip.

## Hauling Actual to Actual (hidden)
Table D-14
Hauling - Actual to Actual Emissions Increases
Salt River Project - Coronado Generating Station
PSD Pollutant | Baseline Actuals (tons/yr) | Representative Actual Annual Emissions (w/o adjustments) (tons/yr) | Representative Actual Emissions with Demand Growth but without Project Increases (tons/yr) | Adjustment Amount (demand growth) (tons/yr) | Representative Actual Annual Emissions without Demand Growth (tons/yr) | Emissions Increase (tons/yr)
PM10 | 28.2259 | #REF! | 30.0823 | 1.8564 | #REF! | #REF!
PM | 105.099 | #REF! | 111.7746 | 6.6756 | #REF! | #REF!
Baseline Actuals (tpy) = (2005 Hauling Baseline Actual Emissions (tpy) + 2006 Hauling Baseline Actual Emissions (tpy)) / 2
Representative Actual Annual Emissions (w/o adjustments) (tpy) = (2017 Hauling Projected Actual Emissions (tpy) + 2018 Hauling Projected Actual Emissions (tpy)) / 2
Representative Actual Emissions with Demand Growth but without Project Increases (tpy) = Baseline Actuals (tpy) x
[Boiler Actual to Actual Representative Actual Annual Emis without Demand Growth / Boiler Actual to Actual Representative Actual Annual Emis w/o Adjustments]
Adjustment Amount = Representative Actual Emissions with Demand Growth but without Project Increases (tpy) - Baseline Actuals (tpy)
Emissions Increase (tpy) = Representative Actual Annual Emissions (w/o adjustments) (tpy) - Baseline Actuals (tpy) - Adjustment Amount (tpy)